## Summary
| Created with: | nPro.energy
| User: | Test
nPro Energy
| Created on: | 09.09.2026 (08:48)
| Project: | Project 1
Diameter | Sections | Length connection pipes | Length distribution pipes | Length | Heat losses | Pressure loss | Water volume | Water mass | Pipe cost | Installation | Pipe cost | Installation | Total cost
DN | - | m | m | m | MWh/a | Pa | m³ | t | €/m | €/m | € | € | €
100 | 5 | 0 | 57.1 | 57.1 | 14.6 | 7633 | 0.41 | 0.41 | 160 | 1100 | 9144 | 62864 | 72008
80 | 6 | 0 | 105.4 | 105.4 | 28.6 | 15931 | 0.52 | 0.53 | 130 | 970 | 13703 | 102243 | 115945
65 | 19 | 0 | 210.9 | 210.9 | 46.9 | 29477 | 0.73 | 0.75 | 113 | 900 | 23832 | 189814 | 213646
50 | 15 | 31.4 | 157.9 | 189.3 | 37.4 | 25064 | 0.41 | 0.42 | 96 | 830 | 18175 | 157141 | 175317
40 | 4 | 0 | 51.3 | 51.3 | 9.1 | 10605 | 0.07 | 0.07 | 87 | 780 | 4438 | 39993 | 44431
32 | 12 | 0 | 151.6 | 151.6 | 23.9 | 29772 | 0.15 | 0.15 | 79 | 740 | 11973 | 112154 | 124128
25 | 48 | 593.5 | 46.7 | 640.2 | 92.6 | 74737 | 0.37 | 0.37 | 79 | 740 | 50576 | 473748 | 524324
Total | 109 | 625 | 781 | 1406 | 253 | 193219 | 2.65 | 2.7 |  |  | 131841 | 1137957 | 1269798

## Detailed list
| Created with: | nPro.energy
| User: | Test
nPro Energy
| Created on: | 09.09.2026 (08:48)
| Project: | Project 1
Pipe ID | Diameter | User-defined diameter | Length | Power | Flow rate | Flow rate | Flow rate | Flow rate | Velocity | Specific pressure loss | Pressure loss | Pipe type | Building connection (option) | Depth | Max. transmittable power | Power reserve | Power reserve | Load factor | Linear heat density | Specific heat loss | Heat losses | Supply temp. | Return temp. | Safety factor | Safety reserve | Geodetic height | Pressure: Supply | Pressure: Return | Laying type | User-defined cost | Existing | Pipe model | Diversity factor | Transferred heat | Inner diameter | Flow rate (simulation) | Pressure loss (simulation) | Pressure: Supply (simulation) | Pressure: Return (simulation) | Start node | End node
- | DN | - | m | kW | m³/d | m³/h | l/h | l/s | m/s | Pa/m | Pa | - | - | m | kW | kW | % | % | MWh/m | kWh/m | MWh/a | °C | °C | - | kW | m | bar | bar | - | €/m | - | - | - | MWh | mm | l/h | Pa | bar | bar | - | -
71 | 100 | No | 4.4 | 689 | 724 | 30 | 30185 | 8.38 | 0.96 | 97 | 421 | Distribution | Auto | 1 | 1037 | 348 | 50.6 | 66.4 | 0.5 | 286.8 | 1.2 | 75 | 53.7 | 1 | --- | 57.1 | 4.91 | 3.21 | Soil | --- | No | Rohrmodell 1 | 0.801 | 581.831 | 105.3 | 19473 | 179 | 4.32 | 3.16 | 8 | 11
77 | 100 | No | 16.9 | 689 | 724 | 30 | 30185 | 8.38 | 0.96 | 97 | 1634 | Distribution | Auto | 1 | 1037 | 348 | 50.6 | 66.4 | 0.5 | 286.8 | 4.8 | 75 | 53.7 | 1 | --- | 57.1 | 4.92 | 3.2 | Soil | --- | No | Rohrmodell 1 | 0.801 | 581.831 | 105.3 | 19473 | 696 | 4.33 | 3.15 | 5 | 8
85 | 100 | Yes | 13.2 | 689 | 724 | 30 | 30185 | 8.38 | 1.32 | 151 | 1980 | Distribution | Auto | 1.2 | 758 | 69 | 10 | 90.9 | 0.4 | 236.6 | 3.1 | 75 | 53.6 | 1 | --- | 57.2 | 4.95 | 3.18 | Soil | --- | No | Kunststoff (Einzelrohr): BruggPipes: CALPEX UNO (normal) | 0.801 | 581.831 | 90 | 19473 | 895 | 4.35 | 3.15 | 3 | 5
90 | 100 | Yes | 17.3 | 689 | 724 | 30 | 30185 | 8.38 | 1.32 | 151 | 2602 | Distribution | Auto | 1.2 | 758 | 69 | 10 | 90.9 | 0.4 | 236.6 | 4.1 | 75 | 53.6 | 1 | --- | 57.3 | 4.97 | 3.14 | Soil | --- | No | Kunststoff (Einzelrohr): BruggPipes: CALPEX UNO (normal) | 0.801 | 581.831 | 90 | 19473 | 1176 | 4.35 | 3.13 | 2 | 3
96 | 100 | Yes | 5.5 | 765 | 805 | 34 | 33532 | 9.31 | 1.46 | 182 | 995 | Distribution | Auto | 1.2 | 758 | -7 | -1 | 101 | 0.5 | 236.6 | 1.3 | 75 | 53.7 | 1 | --- | 57.3 | 4.99 | 3.12 | Soil | --- | No | Kunststoff (Einzelrohr): BruggPipes: CALPEX UNO (normal) | 0.794 | 690.961 | 90 | 21777 | 454 | 4.36 | 3.12 | EHCurt-Stenvert-Bogen 19 | 2
72 | 80 | No | 22.9 | 505 | 531 | 22 | 22141 | 6.15 | 1.23 | 220 | 5042 | Distribution | Auto | 1 | 506 | 1 | 0.3 | 99.7 | 0.4 | 277.4 | 6.4 | 74.9 | 53.8 | 1 | --- | 57 | 4.88 | 3.25 | Ambient air | --- | No | Rohrmodell 1 | 0.962 | 356.401 | 79.9 | 13901 | 2028 | 4.32 | 3.18 | 11 | 14
80 | 80 | No | 14.6 | 486 | 512 | 21 | 21316 | 5.92 | 1.18 | 204 | 2980 | Distribution | Auto | 1 | 506 | 20 | 4.2 | 96 | 0.4 | 277.4 | 4 | 74.9 | 53.8 | 1 | --- | 57 | 4.83 | 3.3 | Ambient air | --- | No | Rohrmodell 1 | 0.965 | 337.756 | 79.9 | 13530 | 1225 | 4.3 | 3.2 | 14 | 18
83 | 80 | No | 4.1 | 486 | 512 | 21 | 21316 | 5.92 | 1.18 | 204 | 845 | Distribution | Auto | 1 | 506 | 20 | 4.2 | 96 | 0.4 | 277.4 | 1.1 | 74.9 | 53.8 | 1 | --- | 57 | 4.81 | 3.33 | Ambient air | --- | No | Rohrmodell 1 | 0.965 | 337.756 | 79.9 | 13530 | 347 | 4.29 | 3.21 | 18 | 21
94 | 80 | No | 49.1 | 358 | 376 | 16 | 15676 | 4.35 | 0.87 | 112 | 5497 | Distribution | Auto | 1 | 506 | 149 | 41.6 | 70.6 | 0.4 | 277.4 | 13.6 | 74.9 | 53.8 | 1 | --- | 57 | 4.77 | 3.37 | Ambient air | --- | No | Rohrmodell 1 | 0.999 | 211.372 | 79.9 | 10084 | 2332 | 4.27 | 3.23 | 21 | 24
106 | 80 | No | 6.4 | 337 | 354 | 15 | 14760 | 4.1 | 0.82 | 100 | 636 | Distribution | Auto | 1 | 506 | 170 | 50.4 | 66.5 | 0.4 | 232.9 | 1.5 | 74.8 | 53.8 | 1 | --- | 56.4 | 4.78 | 3.47 | Soil | --- | No | Rohrmodell 1 | 0.999 | 199.393 | 79.9 | 9514 | 271 | 4.31 | 3.31 | 28 | 32
108 | 80 | No | 8.3 | 358 | 376 | 16 | 15676 | 4.35 | 0.87 | 112 | 931 | Distribution | Auto | 1 | 506 | 149 | 41.6 | 70.6 | 0.4 | 232.9 | 1.9 | 74.8 | 53.9 | 1 | --- | 56.4 | 4.79 | 3.46 | Soil | --- | No | Rohrmodell 1 | 0.999 | 211.372 | 79.9 | 10084 | 395 | 4.31 | 3.3 | 24 | 28
19 | 65 | No | 19.6 | 188 | 198 | 8 | 8246 | 2.29 | 0.65 | 79 | 1544 | Distribution | Auto | 0.9 | 325 | 137 | 72.9 | 57.8 | 0.6 | 222.3 | 4.3 | 74.6 | 53.3 | 1 | --- | 57 | 4.69 | 3.43 | Soil | --- | No | Rohrmodell 1 | 1 | 122.717 | 67.1 | 2999 | 224 | 4.28 | 3.2 | 65 | 69
20 | 65 | No | 8.7 | 188 | 198 | 8 | 8246 | 2.29 | 0.65 | 79 | 688 | Distribution | Auto | 0.9 | 325 | 137 | 72.9 | 57.8 | 0.5 | 222.3 | 1.9 | 74.7 | 53.2 | 1 | --- | 57.1 | 4.69 | 3.4 | Soil | --- | No | Rohrmodell 1 | 1 | 122.717 | 67.1 | 2999 | 100 | 4.28 | 3.18 | 59 | 65
23 | 65 | No | 9.8 | 209 | 220 | 9 | 9162 | 2.55 | 0.72 | 97 | 948 | Distribution | Auto | 0.9 | 325 | 116 | 55.6 | 64.3 | 0.5 | 222.3 | 2.2 | 74.7 | 53.3 | 1 | --- | 57.1 | 4.7 | 3.39 | Soil | --- | No | Rohrmodell 1 | 1 | 139.893 | 67.1 | 3429 | 144 | 4.28 | 3.18 | 54 | 59
25 | 65 | No | 5.6 | 209 | 220 | 9 | 9162 | 2.55 | 0.72 | 97 | 546 | Distribution | Auto | 0.9 | 325 | 116 | 55.6 | 64.3 | 0.5 | 222.3 | 1.3 | 74.7 | 53.3 | 1 | --- | 57.1 | 4.71 | 3.38 | Soil | --- | No | Rohrmodell 1 | 1 | 139.893 | 67.1 | 3429 | 83 | 4.28 | 3.18 | 48 | 54
29 | 65 | No | 10.1 | 230 | 242 | 10 | 10079 | 2.8 | 0.79 | 117 | 1173 | Distribution | Auto | 0.9 | 325 | 95 | 41.5 | 70.7 | 0.5 | 222.3 | 2.2 | 74.8 | 53.3 | 1 | --- | 57.1 | 4.72 | 3.37 | Soil | --- | No | Rohrmodell 1 | 1 | 153.567 | 67.1 | 3771 | 177 | 4.28 | 3.18 | 42 | 48
31 | 65 | No | 6.3 | 241 | 254 | 11 | 10570 | 2.94 | 0.83 | 128 | 811 | Distribution | Auto | 0.9 | 325 | 84 | 34.9 | 74.1 | 0.5 | 222.3 | 1.4 | 74.8 | 53.3 | 1 | --- | 57.1 | 4.73 | 3.36 | Soil | --- | No | Rohrmodell 1 | 0.961 | 163.283 | 67.1 | 4015 | 126 | 4.28 | 3.18 | 36 | 42
35 | 65 | No | 11.1 | 252 | 265 | 11 | 11030 | 3.06 | 0.87 | 139 | 1537 | Distribution | Auto | 0.9 | 325 | 74 | 29.3 | 77.4 | 0.5 | 222.3 | 2.5 | 74.8 | 53.3 | 1 | --- | 57.1 | 4.75 | 3.35 | Soil | --- | No | Rohrmodell 1 | 0.926 | 173.226 | 67.1 | 4264 | 246 | 4.29 | 3.18 | 30 | 36
38 | 65 | No | 6.1 | 267 | 280 | 12 | 11686 | 3.25 | 0.92 | 156 | 956 | Distribution | Auto | 0.9 | 325 | 59 | 22 | 82 | 0.5 | 222.3 | 1.4 | 74.8 | 53.4 | 1 | --- | 57 | 4.77 | 3.34 | Soil | --- | No | Rohrmodell 1 | 0.911 | 191.532 | 67.1 | 4722 | 166 | 4.3 | 3.18 | 27 | 30
42 | 65 | No | 6.7 | 267 | 280 | 12 | 11686 | 3.25 | 0.92 | 156 | 1049 | Distribution | Auto | 0.9 | 325 | 59 | 22 | 82 | 0.5 | 222.3 | 1.5 | 74.8 | 53.4 | 1 | --- | 57 | 4.79 | 3.33 | Soil | --- | No | Rohrmodell 1 | 0.911 | 191.532 | 67.1 | 4722 | 182 | 4.3 | 3.18 | 23 | 27
47 | 65 | No | 16.4 | 281 | 295 | 12 | 12307 | 3.42 | 0.97 | 172 | 2833 | Distribution | Auto | 0.9 | 325 | 45 | 15.9 | 86.3 | 0.5 | 222.3 | 3.7 | 74.9 | 53.4 | 1 | --- | 57 | 4.81 | 3.3 | Soil | --- | No | Rohrmodell 1 | 0.895 | 208.707 | 67.1 | 5152 | 524 | 4.3 | 3.18 | 20 | 23
54 | 65 | No | 9.3 | 294 | 310 | 13 | 12909 | 3.59 | 1.01 | 189 | 1761 | Distribution | Auto | 0.9 | 325 | 31 | 10.5 | 90.5 | 0.5 | 222.3 | 2.1 | 74.9 | 53.5 | 1 | --- | 57 | 4.84 | 3.28 | Soil | --- | No | Rohrmodell 1 | 0.881 | 225.43 | 67.1 | 5571 | 345 | 4.31 | 3.17 | 15 | 20
64 | 65 | No | 22.5 | 294 | 310 | 13 | 12909 | 3.59 | 1.01 | 189 | 4258 | Distribution | Auto | 0.9 | 325 | 31 | 10.5 | 90.5 | 0.5 | 222.3 | 5 | 74.9 | 53.4 | 1 | --- | 57 | 4.88 | 3.24 | Soil | --- | No | Rohrmodell 1 | 0.881 | 225.43 | 67.1 | 5571 | 834 | 4.32 | 3.16 | 11 | 15
79 | 65 | No | 14.9 | 190 | 200 | 8 | 8346 | 2.32 | 0.66 | 81 | 1200 | Distribution | Auto | 0.9 | 325 | 135 | 70.8 | 58.5 | 0.4 | 222.3 | 3.3 | 74.7 | 53.7 | 1 | --- | 56.9 | 4.58 | 3.55 | Soil | --- | No | Rohrmodell 1 | 0.999 | 115.882 | 67.1 | 5545 | 545 | 4.19 | 3.31 | 67 | 71
82 | 65 | No | 6.4 | 211 | 222 | 9 | 9262 | 2.57 | 0.73 | 99 | 632 | Distribution | Auto | 0.9 | 325 | 114 | 53.9 | 65 | 0.4 | 222.3 | 1.4 | 74.7 | 53.7 | 1 | --- | 56.8 | 4.6 | 3.55 | Soil | --- | No | Rohrmodell 1 | 0.999 | 127.747 | 67.1 | 6109 | 282 | 4.21 | 3.31 | 61 | 67
86 | 65 | No | 14.9 | 232 | 244 | 10 | 10179 | 2.83 | 0.8 | 119 | 1768 | Distribution | Auto | 0.9 | 325 | 93 | 40.1 | 71.4 | 0.4 | 222.3 | 3.3 | 74.7 | 53.8 | 1 | --- | 56.6 | 4.64 | 3.56 | Soil | --- | No | Rohrmodell 1 | 0.999 | 139.726 | 67.1 | 6678 | 780 | 4.23 | 3.33 | 56 | 61
88 | 65 | No | 6.4 | 253 | 266 | 11 | 11095 | 3.08 | 0.87 | 141 | 899 | Distribution | Auto | 0.9 | 325 | 72 | 28.5 | 77.8 | 0.4 | 222.3 | 1.4 | 74.7 | 53.8 | 1 | --- | 56.5 | 4.66 | 3.55 | Soil | --- | No | Rohrmodell 1 | 0.999 | 151.704 | 67.1 | 7248 | 393 | 4.25 | 3.33 | 50 | 56
91 | 65 | No | 14.9 | 274 | 288 | 12 | 12011 | 3.34 | 0.94 | 164 | 2441 | Distribution | Auto | 0.9 | 325 | 51 | 18.7 | 84.2 | 0.4 | 222.3 | 3.3 | 74.8 | 53.8 | 1 | --- | 56.4 | 4.69 | 3.54 | Soil | --- | No | Rohrmodell 1 | 0.999 | 163.57 | 67.1 | 7812 | 1056 | 4.27 | 3.33 | 44 | 50
97 | 65 | No | 6.4 | 295 | 310 | 13 | 12927 | 3.59 | 1.02 | 190 | 1212 | Distribution | Auto | 0.9 | 325 | 30 | 10.3 | 90.7 | 0.4 | 222.3 | 1.4 | 74.8 | 53.8 | 1 | --- | 56.3 | 4.72 | 3.53 | Soil | --- | No | Rohrmodell 1 | 0.999 | 175.549 | 67.1 | 8381 | 521 | 4.29 | 3.33 | 38 | 44
101 | 65 | No | 14.9 | 316 | 332 | 14 | 13843 | 3.85 | 1.09 | 217 | 3222 | Distribution | Auto | 0.9 | 325 | 9 | 3 | 97.1 | 0.4 | 222.3 | 3.3 | 74.8 | 53.8 | 1 | --- | 56.4 | 4.74 | 3.49 | Soil | --- | No | Rohrmodell 1 | 0.999 | 187.527 | 67.1 | 8951 | 1375 | 4.29 | 3.31 | 32 | 38
8 | 50 | No | 14.4 | 121 | 127 | 5 | 5300 | 1.47 | 0.66 | 112 | 1611 | Connection | Auto | 0.9 | 182 | 61 | 50.4 | 66.5 | 0.8 | 197.8 | 2.8 | 73.8 | 53.2 | --- | 100 | 57.1 | 4.49 | 3.61 | Soil | --- | No | Rohrmodell 1 | 5.785 | 11.979 | 53.1 | 300 | 8 | 4.25 | 3.21 | 97 | Marie-Hüllenkremer-Straße 13
9 | 50 | No | 17 | 121 | 127 | 5 | 5300 | 1.47 | 0.66 | 112 | 1902 | Connection | Auto | 0.9 | 182 | 61 | 50.4 | 66.5 | 0.7 | 197.8 | 3.4 | 73.6 | 52.9 | --- | 100 | 57.2 | 4.47 | 3.61 | Soil | --- | No | Rohrmodell 1 | 5.785 | 11.3 | 53.1 | 283 | 8 | 4.24 | 3.2 | 100 | Marie-Hüllenkremer-Straße 15
10 | 50 | No | 16.9 | 167 | 176 | 7 | 7330 | 2.04 | 0.92 | 210 | 3557 | Distribution | Auto | 0.9 | 182 | 15 | 8.8 | 91.9 | 0.6 | 197.8 | 3.3 | 74.5 | 53.4 | 1 | --- | 57 | 4.66 | 3.46 | Soil | --- | No | Rohrmodell 1 | 1 | 111.871 | 53.1 | 2727 | 527 | 4.28 | 3.2 | 69 | 72
11 | 50 | No | 5.9 | 146 | 154 | 6 | 6414 | 1.78 | 0.8 | 162 | 952 | Distribution | Auto | 0.9 | 182 | 36 | 24.3 | 80.4 | 0.7 | 197.8 | 1.2 | 74.5 | 53.4 | 1 | --- | 57 | 4.63 | 3.49 | Soil | --- | No | Rohrmodell 1 | 1 | 100.005 | 53.1 | 2430 | 147 | 4.28 | 3.2 | 72 | 76
12 | 50 | No | 7.6 | 125 | 132 | 5 | 5497 | 1.53 | 0.69 | 120 | 914 | Distribution | Auto | 0.9 | 182 | 56 | 45 | 69 | 0.7 | 197.8 | 1.5 | 74.5 | 53.3 | 1 | --- | 57 | 4.62 | 3.5 | Soil | --- | No | Rohrmodell 1 | 1 | 87.574 | 53.1 | 2118 | 147 | 4.27 | 3.21 | 76 | 82
13 | 50 | No | 16.2 | 104 | 110 | 5 | 4581 | 1.27 | 0.57 | 84 | 1368 | Distribution | Auto | 0.9 | 182 | 77 | 74 | 57.5 | 0.6 | 197.8 | 3.2 | 74.4 | 53.2 | 1 | --- | 57 | 4.6 | 3.51 | Soil | --- | No | Rohrmodell 1 | 1 | 68.59 | 53.1 | 1665 | 200 | 4.27 | 3.21 | 82 | 85
61 | 50 | No | 14.8 | 107 | 112 | 5 | 4681 | 1.3 | 0.59 | 88 | 1305 | Distribution | Auto | 0.9 | 182 | 75 | 70.3 | 58.7 | 0.3 | 197.8 | 2.9 | 74.6 | 53.6 | 1 | --- | 57.3 | 4.47 | 3.59 | Soil | --- | No | Rohrmodell 1 | 0.998 | 68.419 | 53.1 | 3290 | 662 | 4.12 | 3.3 | 84 | 88
62 | 50 | No | 15 | 104 | 110 | 5 | 4581 | 1.27 | 0.57 | 84 | 1263 | Distribution | Auto | 0.9 | 182 | 77 | 74 | 57.5 | 0.8 | 197.8 | 3 | 74.7 | 53.9 | 1 | --- | 57.7 | 4.63 | 3.35 | Soil | --- | No | Rohrmodell 1 | 1 | 87.911 | 53.1 | 2203 | 312 | 4.18 | 3.16 | 34 | 40
65 | 50 | No | 6.4 | 128 | 134 | 6 | 5597 | 1.55 | 0.7 | 124 | 795 | Distribution | Auto | 0.9 | 182 | 54 | 42.4 | 70.2 | 0.4 | 197.8 | 1.3 | 74.6 | 53.6 | 1 | --- | 57.3 | 4.48 | 3.58 | Soil | --- | No | Rohrmodell 1 | 0.998 | 80.285 | 53.1 | 3854 | 386 | 4.12 | 3.3 | 80 | 84
67 | 50 | No | 16.7 | 125 | 132 | 5 | 5497 | 1.53 | 0.69 | 120 | 2008 | Distribution | Auto | 0.9 | 182 | 56 | 45 | 69 | 0.7 | 197.8 | 3.3 | 74.8 | 53.9 | 1 | --- | 57.5 | 4.67 | 3.35 | Soil | --- | No | Rohrmodell 1 | 1 | 103.505 | 53.1 | 2594 | 474 | 4.21 | 3.18 | 29 | 34
70 | 50 | No | 14.9 | 149 | 156 | 7 | 6514 | 1.81 | 0.82 | 167 | 2486 | Distribution | Auto | 0.9 | 182 | 33 | 22.4 | 81.7 | 0.4 | 197.8 | 2.9 | 74.6 | 53.7 | 1 | --- | 57.1 | 4.52 | 3.58 | Soil | --- | No | Rohrmodell 1 | 0.998 | 92.15 | 53.1 | 4418 | 1170 | 4.15 | 3.31 | 75 | 80
73 | 50 | No | 6.4 | 169 | 178 | 7 | 7430 | 2.06 | 0.93 | 216 | 1380 | Distribution | Auto | 0.9 | 182 | 12 | 7.3 | 93.2 | 0.4 | 197.8 | 1.3 | 74.7 | 53.7 | 1 | --- | 57.1 | 4.55 | 3.55 | Soil | --- | No | Rohrmodell 1 | 0.999 | 104.016 | 53.1 | 4981 | 634 | 4.16 | 3.3 | 71 | 75
76 | 50 | No | 25.6 | 146 | 154 | 6 | 6414 | 1.78 | 0.8 | 162 | 4154 | Distribution | Auto | 0.9 | 182 | 36 | 24.3 | 80.4 | 0.7 | 197.8 | 5.1 | 74.8 | 54 | 1 | --- | 57.2 | 4.74 | 3.34 | Soil | --- | No | Rohrmodell 1 | 1 | 126.384 | 53.1 | 3446 | 1249 | 4.25 | 3.19 | 25 | 29
81 | 50 | No | 5.1 | 146 | 154 | 6 | 6414 | 1.78 | 0.8 | 162 | 829 | Distribution | Auto | 0.9 | 182 | 36 | 24.3 | 80.4 | 0.7 | 197.8 | 1 | 74.9 | 54 | 1 | --- | 57 | 4.79 | 3.33 | Soil | --- | No | Rohrmodell 1 | 1 | 126.384 | 53.1 | 3446 | 249 | 4.28 | 3.2 | 21 | 25
95 | 50 | No | 6.4 | 104 | 110 | 5 | 4581 | 1.27 | 0.57 | 84 | 540 | Distribution | Auto | 0.9 | 182 | 77 | 74 | 57.5 | 1.3 | 197.8 | 1.3 | 75 | 54.4 | 1 | --- | 57.2 | 4.96 | 3.11 | Soil | --- | No | Rohrmodell 1 | 1 | 109.13 | 53.1 | 2305 | 145 | 4.34 | 3.1 | 2 | 4
14 | 40 | No | 15.7 | 84 | 88 | 4 | 3665 | 1.02 | 0.77 | 205 | 3220 | Distribution | Auto | 0.8 | 101 | 18 | 21.3 | 82.5 | 0.6 | 177.4 | 2.8 | 74.3 | 53 | 1 | --- | 57.1 | 4.55 | 3.52 | Soil | --- | No | Rohrmodell 1 | 1 | 50.171 | 41.1 | 1225 | 395 | 4.25 | 3.19 | 85 | 89
56 | 40 | No | 18.9 | 84 | 88 | 4 | 3665 | 1.02 | 0.77 | 205 | 3879 | Distribution | Auto | 0.8 | 101 | 18 | 21.3 | 82.5 | 0.8 | 177.4 | 3.3 | 74.6 | 53.8 | 1 | --- | 57.9 | 4.57 | 3.35 | Soil | --- | No | Rohrmodell 1 | 1 | 70.849 | 41.1 | 1775 | 959 | 4.15 | 3.14 | 40 | 46
58 | 40 | No | 6.4 | 86 | 90 | 4 | 3765 | 1.05 | 0.79 | 217 | 1384 | Distribution | Auto | 0.8 | 101 | 16 | 18.1 | 84.7 | 0.3 | 177.4 | 1.1 | 74.5 | 53.6 | 1 | --- | 57.3 | 4.44 | 3.6 | Soil | --- | No | Rohrmodell 1 | 0.997 | 56.553 | 41.1 | 2726 | 740 | 4.1 | 3.3 | 88 | 92
100 | 40 | No | 10.3 | 84 | 88 | 4 | 3665 | 1.02 | 0.77 | 205 | 2122 | Distribution | Auto | 0.8 | 101 | 18 | 21.3 | 82.5 | 1.4 | 177.4 | 1.8 | 74.9 | 54.4 | 1 | --- | 57.1 | 4.95 | 3.13 | Soil | --- | No | Rohrmodell 1 | 1 | 91.276 | 41.1 | 1927 | 614 | 4.33 | 3.11 | 4 | 6
15 | 32 | No | 13.8 | 63 | 66 | 3 | 2749 | 0.76 | 0.75 | 233 | 3229 | Distribution | Auto | 0.8 | 71 | 9 | 13.7 | 88 | 0.6 | 157.6 | 2.2 | 74.1 | 53.1 | 1 | --- | 57.1 | 4.51 | 3.56 | Soil | --- | No | Rohrmodell 1 | 1 | 41.697 | 36 | 1023 | 485 | 4.24 | 3.2 | 89 | 93
16 | 32 | No | 5.5 | 42 | 44 | 2 | 1832 | 0.51 | 0.5 | 106 | 581 | Distribution | Auto | 0.8 | 71 | 29 | 70.5 | 58.7 | 0.6 | 157.6 | 0.9 | 74 | 52.7 | 1 | --- | 57.1 | 4.49 | 3.59 | Soil | --- | No | Rohrmodell 1 | 1 | 23.279 | 36 | 583 | 67 | 4.24 | 3.2 | 93 | 97
28 | 32 | No | 16.9 | 39 | 41 | 2 | 1725 | 0.48 | 0.47 | 95 | 1604 | Distribution | Auto | 0.8 | 71 | 32 | 81 | 55.2 | 0.5 | 157.5 | 2.7 | 74.3 | 53.8 | 1 | --- | 57.1 | 4.23 | 3.85 | Soil | --- | No | Rohrmodell 1 | 1 | 30.368 | 36 | 1588 | 1368 | 3.91 | 3.53 | 105 | 106
34 | 32 | No | 21.8 | 65 | 68 | 3 | 2849 | 0.79 | 0.78 | 250 | 5452 | Distribution | Auto | 0.8 | 71 | 6 | 9.7 | 91.2 | 0.6 | 157.5 | 3.4 | 74.3 | 53.8 | 1 | --- | 57 | 4.28 | 3.81 | Soil | --- | No | Rohrmodell 1 | 0.996 | 54.348 | 36 | 2722 | 4989 | 3.96 | 3.5 | 104 | 105
40 | 32 | No | 8.8 | 65 | 68 | 3 | 2849 | 0.79 | 0.78 | 250 | 2203 | Distribution | Auto | 0.8 | 71 | 6 | 9.7 | 91.2 | 0.5 | 157.5 | 1.4 | 74.4 | 53.8 | 1 | --- | 57 | 4.33 | 3.76 | Soil | --- | No | Rohrmodell 1 | 0.996 | 54.348 | 36 | 2722 | 2015 | 4.01 | 3.46 | 102 | 104
43 | 32 | No | 6.8 | 65 | 68 | 3 | 2849 | 0.79 | 0.78 | 250 | 1701 | Distribution | Auto | 0.8 | 71 | 6 | 9.7 | 91.2 | 0.5 | 157.6 | 1.1 | 74.4 | 53.8 | 1 | --- | 57 | 4.36 | 3.74 | Soil | --- | No | Rohrmodell 1 | 0.996 | 54.348 | 36 | 2722 | 1556 | 4.03 | 3.43 | 99 | 102
45 | 32 | No | 17.6 | 42 | 44 | 2 | 1832 | 0.51 | 0.5 | 106 | 1876 | Distribution | Auto | 0.8 | 71 | 29 | 70.5 | 58.7 | 0.8 | 157.5 | 2.8 | 74.4 | 53.8 | 1 | --- | 57.8 | 4.5 | 3.44 | Soil | --- | No | Rohrmodell 1 | 1 | 36.047 | 36 | 904 | 489 | 4.14 | 3.17 | 52 | 58
48 | 32 | No | 6.2 | 65 | 68 | 3 | 2849 | 0.79 | 0.78 | 250 | 1561 | Distribution | Auto | 0.8 | 71 | 6 | 9.7 | 91.2 | 0.5 | 157.6 | 1 | 74.4 | 53.8 | 1 | --- | 57 | 4.38 | 3.72 | Soil | --- | No | Rohrmodell 1 | 0.996 | 54.348 | 36 | 2722 | 1428 | 4.05 | 3.41 | 96 | 99
49 | 32 | No | 15.3 | 63 | 66 | 3 | 2749 | 0.76 | 0.75 | 233 | 3563 | Distribution | Auto | 0.8 | 71 | 9 | 13.7 | 88 | 0.8 | 157.6 | 2.4 | 74.5 | 53.8 | 1 | --- | 58 | 4.51 | 3.39 | Soil | --- | No | Rohrmodell 1 | 1 | 52.656 | 36 | 1320 | 867 | 4.13 | 3.14 | 46 | 52
52 | 32 | No | 23.8 | 65 | 68 | 3 | 2849 | 0.79 | 0.78 | 250 | 5958 | Distribution | Auto | 0.8 | 71 | 6 | 9.7 | 91.2 | 0.4 | 157.5 | 3.8 | 74.5 | 53.7 | 1 | --- | 57.2 | 4.41 | 3.65 | Soil | --- | No | Rohrmodell 1 | 0.996 | 54.348 | 36 | 2722 | 5452 | 4.07 | 3.35 | 92 | 96
103 | 32 | No | 3.6 | 63 | 66 | 3 | 2749 | 0.76 | 0.75 | 233 | 832 | Distribution | Auto | 0.8 | 71 | 9 | 13.7 | 88 | 1.4 | 157.6 | 0.6 | 74.9 | 54.4 | 1 | --- | 56.8 | 4.96 | 3.18 | Soil | --- | No | Rohrmodell 1 | 1 | 72.178 | 36 | 1523 | 266 | 4.36 | 3.14 | 6 | 10
107 | 32 | No | 11.4 | 42 | 44 | 2 | 1832 | 0.51 | 0.5 | 106 | 1213 | Distribution | Auto | 0.8 | 71 | 29 | 70.5 | 58.7 | 1.6 | 157.6 | 1.8 | 74.8 | 54.5 | 1 | --- | 56.8 | 4.95 | 3.19 | Soil | --- | No | Rohrmodell 1 | 1 | 50.707 | 36 | 1069 | 434 | 4.35 | 3.15 | 10 | 12
1 | 25 | No | 8.6 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1002 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.3 | 144.6 | 1.2 | 74 | 53.8 | 1 | --- | 56.8 | 4.66 | 3.47 | Soil | --- | No | Rohrmodell 1 | 1 | 10.847 | 27.3 | 272 | 104 | 4.29 | 3.21 | 73 | Marie-Hüllenkremer-Straße 1
2 | 25 | No | 14.1 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1647 | Distribution | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.5 | 144.6 | 2 | 74.4 | 53.5 | 1 | --- | 56.8 | 4.68 | 3.46 | Soil | --- | No | Rohrmodell 1 | 1 | 10.847 | 27.3 | 272 | 171 | 4.29 | 3.21 | 69 | 73
3 | 25 | No | 10.4 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1210 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.1 | 144.6 | 1.5 | 74.4 | 54.1 | 1 | --- | 57 | 4.62 | 3.48 | Soil | --- | No | Rohrmodell 1 | 1 | 11.866 | 27.3 | 297 | 147 | 4.27 | 3.2 | 72 | Marie-Hüllenkremer-Straße 1a
4 | 25 | No | 10.6 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1241 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.7 | 144.6 | 1.5 | 74.2 | 54 | 1 | --- | 57.1 | 4.57 | 3.51 | Soil | --- | No | Rohrmodell 1 | 1 | 18.419 | 27.3 | 440 | 310 | 4.25 | 3.19 | 85 | Marie-Hüllenkremer-Straße 5
5 | 25 | No | 9.5 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1110 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 2 | 144.6 | 1.4 | 74.4 | 54.2 | 1 | --- | 57 | 4.59 | 3.5 | Soil | --- | No | Rohrmodell 1 | 1 | 18.984 | 27.3 | 453 | 294 | 4.26 | 3.2 | 82 | Marie-Hüllenkremer-Straße 3
6 | 25 | No | 9.8 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1143 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.9 | 144.6 | 1.4 | 74 | 53.6 | 1 | --- | 57.1 | 4.53 | 3.55 | Soil | --- | No | Rohrmodell 1 | 1 | 8.474 | 27.3 | 203 | 68 | 4.25 | 3.2 | 89 | Marie-Hüllenkremer-Straße 7
7 | 25 | No | 9.8 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1147 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.9 | 144.6 | 1.4 | 74 | 53.8 | 1 | --- | 57.1 | 4.49 | 3.59 | Soil | --- | No | Rohrmodell 1 | 1 | 18.419 | 27.3 | 440 | 287 | 4.24 | 3.2 | 93 | Marie-Hüllenkremer-Straße 11
17 | 25 | No | 4.7 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 545 | Distribution | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.5 | 144.6 | 0.7 | 73.9 | 52.5 | 1 | --- | 57.1 | 4.48 | 3.59 | Soil | --- | No | Rohrmodell 1 | 1 | 11.3 | 27.3 | 283 | 61 | 4.24 | 3.2 | 97 | 100
18 | 25 | No | 10.6 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1235 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.2 | 144.6 | 1.5 | 74.3 | 54.1 | 1 | --- | 57 | 4.6 | 3.49 | Soil | --- | No | Rohrmodell 1 | 1 | 12.431 | 27.3 | 312 | 164 | 4.26 | 3.2 | 76 | Curt-Stenvert-Bogen 1
21 | 25 | No | 15.9 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1856 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.1 | 144.6 | 2.3 | 74.5 | 54.2 | 1 | --- | 57.1 | 4.68 | 3.4 | Soil | --- | No | Rohrmodell 1 | 1 | 17.175 | 27.3 | 430 | 446 | 4.26 | 3.18 | 59 | Curt-Stenvert-Bogen 3
22 | 25 | No | 13.3 | 18 | 19 | 1 | 809 | 0.22 | 0.38 | 92 | 1223 | Connection | Auto | 0.8 | 34 | 16 | 84.6 | 54.2 | 1.1 | 144.6 | 1.9 | 74 | 53.9 | 1 | --- | 57.1 | 4.2 | 3.88 | Soil | --- | No | Rohrmodell 1 | 1 | 13.983 | 27.3 | 809 | 1223 | 3.88 | 3.56 | 108 | Marie-Hüllenkremer-Straße 23
24 | 25 | No | 15.1 | 18 | 19 | 1 | 809 | 0.22 | 0.38 | 92 | 1392 | Distribution | Auto | 0.8 | 34 | 16 | 84.6 | 54.2 | 0.5 | 144.6 | 2.2 | 74.1 | 53.7 | 1 | --- | 57.1 | 4.21 | 3.86 | Soil | --- | No | Rohrmodell 1 | 1 | 13.983 | 27.3 | 809 | 1392 | 3.89 | 3.55 | 106 | 108
26 | 25 | No | 13.7 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1594 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.2 | 144.6 | 2 | 74.1 | 54 | 1 | --- | 57.1 | 4.21 | 3.87 | Soil | --- | No | Rohrmodell 1 | 1 | 16.384 | 27.3 | 779 | 1170 | 3.9 | 3.55 | 106 | Marie-Hüllenkremer-Straße 25
27 | 25 | No | 15.9 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1855 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.9 | 144.6 | 2.3 | 74.6 | 54.2 | 1 | --- | 57.1 | 4.69 | 3.38 | Soil | --- | No | Rohrmodell 1 | 1 | 13.674 | 27.3 | 342 | 292 | 4.27 | 3.17 | 48 | Curt-Stenvert-Bogen 5
30 | 25 | No | 16 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1863 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.6 | 144.6 | 2.3 | 74.5 | 54 | 1 | --- | 57.1 | 4.71 | 3.37 | Soil | --- | No | Rohrmodell 1 | 1 | 9.716 | 27.3 | 243 | 154 | 4.27 | 3.17 | 42 | Curt-Stenvert-Bogen 7
32 | 25 | No | 13 | 26 | 27 | 1 | 1133 | 0.31 | 0.54 | 175 | 2287 | Connection | Auto | 0.8 | 34 | 8 | 31.8 | 75.9 | 1.8 | 144.6 | 1.9 | 74.3 | 54.2 | 1 | --- | 57.1 | 4.23 | 3.85 | Soil | --- | No | Rohrmodell 1 | 1 | 23.98 | 27.3 | 1133 | 2287 | 3.91 | 3.54 | 105 | Marie-Hüllenkremer-Straße 27
33 | 25 | No | 16 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1865 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.6 | 144.6 | 2.3 | 74.5 | 54 | 1 | --- | 57.1 | 4.72 | 3.36 | Soil | --- | No | Rohrmodell 1 | 1 | 9.943 | 27.3 | 249 | 165 | 4.27 | 3.17 | 36 | Curt-Stenvert-Bogen 9
36 | 25 | No | 6.7 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 776 | Connection | Yes | 0.8 | 34 | 13 | 63.1 | 61.3 | 2.8 | 144.6 | 1 | 74 | 53.9 | 1 | --- | 57.7 | 4.47 | 3.49 | Soil | --- | No | Rohrmodell 1 | 1 | 18.419 | 27.3 | 462 | 212 | 4.14 | 3.19 | 63 | Marie-Hüllenkremer-Straße 16
37 | 25 | No | 16.5 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1925 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.1 | 144.6 | 2.4 | 74.7 | 54.4 | 1 | --- | 57 | 4.75 | 3.35 | Soil | --- | No | Rohrmodell 1 | 1 | 18.306 | 27.3 | 459 | 521 | 4.28 | 3.18 | 30 | Curt-Stenvert-Bogen 11a
39 | 25 | No | 12.8 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1492 | Distribution | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.9 | 144.6 | 1.8 | 74.2 | 53.7 | 1 | --- | 57.7 | 4.49 | 3.47 | Soil | --- | No | Rohrmodell 1 | 1 | 18.419 | 27.3 | 462 | 408 | 4.14 | 3.19 | 58 | 63
41 | 25 | No | 6.7 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 785 | Connection | Yes | 0.8 | 34 | 13 | 63.1 | 61.3 | 2.6 | 144.6 | 1 | 74.2 | 54.1 | 1 | --- | 57.8 | 4.48 | 3.46 | Soil | --- | No | Rohrmodell 1 | 1 | 17.628 | 27.3 | 442 | 198 | 4.13 | 3.18 | 58 | Marie-Hüllenkremer-Straße 18
44 | 25 | No | 16.7 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1943 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1 | 144.6 | 2.4 | 74.7 | 54.4 | 1 | --- | 57 | 4.77 | 3.32 | Soil | --- | No | Rohrmodell 1 | 1 | 17.175 | 27.3 | 430 | 466 | 4.29 | 3.17 | 23 | Curt-Stenvert-Bogen 11
46 | 25 | No | 6.8 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 793 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 2.4 | 144.6 | 1 | 74.4 | 54.3 | 1 | --- | 58 | 4.49 | 3.42 | Soil | --- | No | Rohrmodell 1 | 1 | 16.61 | 27.3 | 416 | 179 | 4.12 | 3.15 | 52 | Marie-Hüllenkremer-Straße 20
50 | 25 | No | 6.9 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 806 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 2.6 | 144.6 | 1 | 74.5 | 54.4 | 1 | --- | 57.9 | 4.54 | 3.38 | Soil | --- | No | Rohrmodell 1 | 1 | 18.193 | 27.3 | 455 | 215 | 4.14 | 3.15 | 46 | Marie-Hüllenkremer-Straße 22
51 | 25 | No | 18.6 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2170 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.1 | 144.6 | 2.7 | 59.3 | 8.9 | 1 | --- | 57.2 | 4.43 | 3.63 | Soil | --- | No | Rohrmodell 1 | 1 | 2.206 | 27.3 | 5 | 1 | 4.1 | 3.32 | 92 | Marie-Hüllenkremer-Straße 29
53 | 25 | No | 16.5 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1924 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1 | 144.6 | 2.4 | 74.7 | 54.4 | 1 | --- | 57 | 4.81 | 3.29 | Soil | --- | No | Rohrmodell 1 | 1 | 16.723 | 27.3 | 419 | 440 | 4.29 | 3.17 | 20 | Curt-Stenvert-Bogen 13
55 | 25 | No | 18.6 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2166 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.6 | 144.6 | 2.7 | 74.4 | 54.2 | 1 | --- | 57.3 | 4.44 | 3.6 | Soil | --- | No | Rohrmodell 1 | 1 | 11.866 | 27.3 | 564 | 862 | 4.1 | 3.3 | 88 | Marie-Hüllenkremer-Straße 31
57 | 25 | No | 7 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 819 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 2.4 | 144.6 | 1 | 74.6 | 54.5 | 1 | --- | 57.7 | 4.61 | 3.35 | Soil | --- | No | Rohrmodell 1 | 1 | 17.062 | 27.3 | 427 | 194 | 4.17 | 3.16 | 40 | Marie-Hüllenkremer-Straße 24
59 | 25 | No | 18.5 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2160 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.6 | 144.6 | 2.7 | 74.5 | 54.2 | 1 | --- | 57.3 | 4.45 | 3.59 | Soil | --- | No | Rohrmodell 1 | 1 | 11.866 | 27.3 | 564 | 859 | 4.11 | 3.3 | 84 | Marie-Hüllenkremer-Straße 33
60 | 25 | No | 18.5 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2155 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.6 | 144.6 | 2.7 | 74.5 | 54.2 | 1 | --- | 57.3 | 4.46 | 3.58 | Soil | --- | No | Rohrmodell 1 | 1 | 11.866 | 27.3 | 564 | 858 | 4.11 | 3.29 | 80 | Marie-Hüllenkremer-Straße 35
63 | 25 | No | 8.1 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 946 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.9 | 144.6 | 1.2 | 74.7 | 54.5 | 1 | --- | 57.5 | 4.64 | 3.36 | Soil | --- | No | Rohrmodell 1 | 1 | 15.594 | 27.3 | 391 | 190 | 4.19 | 3.17 | 34 | Marie-Hüllenkremer-Straße 26
66 | 25 | No | 18.4 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2150 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.6 | 144.6 | 2.7 | 74.5 | 54.3 | 1 | --- | 57.1 | 4.51 | 3.56 | Soil | --- | No | Rohrmodell 1 | 1 | 11.866 | 27.3 | 564 | 855 | 4.15 | 3.3 | 75 | Marie-Hüllenkremer-Straße 37
68 | 25 | No | 7.2 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 839 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 3.2 | 144.6 | 1 | 74.8 | 54.7 | 1 | --- | 57.2 | 4.7 | 3.36 | Soil | --- | No | Rohrmodell 1 | 1 | 22.879 | 27.3 | 853 | 732 | 4.22 | 3.2 | 29 | Marie-Hüllenkremer-Straße 28
69 | 25 | No | 18.4 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2145 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.6 | 144.6 | 2.7 | 74.5 | 54.3 | 1 | --- | 57.1 | 4.53 | 3.55 | Soil | --- | No | Rohrmodell 1 | 1 | 11.866 | 27.3 | 564 | 853 | 4.15 | 3.29 | 71 | Marie-Hüllenkremer-Straße 39
74 | 25 | No | 11.5 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1346 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.6 | 144.6 | 1.7 | 74.8 | 54.6 | 1 | --- | 57 | 4.82 | 3.27 | Soil | --- | No | Rohrmodell 1 | 1 | 18.645 | 27.3 | 371 | 246 | 4.29 | 3.18 | 14 | Marie-Hüllenkremer-Straße 32
75 | 25 | No | 18.3 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2139 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.6 | 144.6 | 2.7 | 74.6 | 54.3 | 1 | --- | 56.9 | 4.56 | 3.55 | Soil | --- | No | Rohrmodell 1 | 1 | 11.866 | 27.3 | 564 | 851 | 4.18 | 3.3 | 67 | Marie-Hüllenkremer-Straße 41
78 | 25 | No | 18.3 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2134 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.7 | 144.6 | 2.6 | 74.6 | 54.3 | 1 | --- | 56.8 | 4.58 | 3.55 | Soil | --- | No | Rohrmodell 1 | 1 | 11.979 | 27.3 | 569 | 865 | 4.19 | 3.31 | 61 | Marie-Hüllenkremer-Straße 43
84 | 25 | No | 18.2 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2128 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.7 | 144.6 | 2.6 | 74.6 | 54.4 | 1 | --- | 56.6 | 4.62 | 3.55 | Soil | --- | No | Rohrmodell 1 | 1 | 11.979 | 27.3 | 569 | 863 | 4.22 | 3.32 | 56 | Marie-Hüllenkremer-Straße 45
87 | 25 | No | 18.2 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2124 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.7 | 144.6 | 2.6 | 74.6 | 54.4 | 1 | --- | 56.5 | 4.64 | 3.55 | Soil | --- | No | Rohrmodell 1 | 1 | 11.866 | 27.3 | 564 | 845 | 4.24 | 3.32 | 50 | Marie-Hüllenkremer-Straße 47
89 | 25 | No | 18.2 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2118 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.7 | 144.6 | 2.6 | 74.6 | 54.4 | 1 | --- | 56.4 | 4.68 | 3.53 | Soil | --- | No | Rohrmodell 1 | 1 | 11.979 | 27.3 | 569 | 859 | 4.26 | 3.32 | 44 | Marie-Hüllenkremer-Straße 49
92 | 25 | No | 18.1 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2114 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.7 | 144.6 | 2.6 | 74.7 | 54.4 | 1 | --- | 56.3 | 4.71 | 3.52 | Soil | --- | No | Rohrmodell 1 | 1 | 11.979 | 27.3 | 569 | 857 | 4.27 | 3.32 | 38 | Marie-Hüllenkremer-Straße 51
93 | 25 | No | 11.7 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1369 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.5 | 144.6 | 1.7 | 74.8 | 54.6 | 1 | --- | 57.2 | 4.94 | 3.11 | Soil | --- | No | Rohrmodell 1 | 1 | 17.854 | 27.3 | 377 | 258 | 4.33 | 3.1 | 4 | Marie-Hüllenkremer-Straße 61
98 | 25 | No | 18.1 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2110 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.7 | 144.6 | 2.6 | 74.7 | 54.4 | 1 | --- | 56.4 | 4.74 | 3.47 | Soil | --- | No | Rohrmodell 1 | 1 | 11.866 | 27.3 | 564 | 840 | 4.28 | 3.29 | 32 | Marie-Hüllenkremer-Straße 53
99 | 25 | No | 15.5 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1809 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 1.4 | 144.6 | 2.2 | 74.8 | 54.5 | 1 | --- | 57 | 4.92 | 3.17 | Soil | --- | No | Rohrmodell 1 | 1 | 21.471 | 27.3 | 454 | 481 | 4.33 | 3.13 | 10 | Marie-Hüllenkremer-Straße 59
102 | 25 | No | 18 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 2105 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 0.7 | 144.6 | 2.6 | 74.7 | 54.4 | 1 | --- | 56.4 | 4.75 | 3.46 | Soil | --- | No | Rohrmodell 1 | 1 | 11.979 | 27.3 | 569 | 854 | 4.29 | 3.29 | 28 | Marie-Hüllenkremer-Straße 55
104 | 25 | No | 5.2 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 605 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 3.7 | 144.6 | 0.8 | 74.9 | 54.8 | 1 | --- | 57.1 | 4.93 | 3.15 | Soil | --- | No | Rohrmodell 1 | 1 | 19.098 | 27.3 | 404 | 129 | 4.33 | 3.11 | 6 | Curt-Stenvert-Bogen 17
105 | 25 | No | 15.3 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 1780 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 2 | 144.6 | 2.2 | 74.7 | 54.5 | 1 | --- | 56.8 | 4.93 | 3.21 | Soil | --- | No | Rohrmodell 1 | 1 | 30.14 | 27.3 | 634 | 884 | 4.34 | 3.15 | 12 | Marie-Hüllenkremer-Straße 57
109 | 25 | No | 5.5 | 21 | 22 | 1 | 916 | 0.25 | 0.43 | 117 | 647 | Connection | Auto | 0.8 | 34 | 13 | 63.1 | 61.3 | 3.7 | 144.6 | 0.8 | 74.8 | 54.7 | 1 | --- | 56.8 | 4.93 | 3.2 | Soil | --- | No | Rohrmodell 1 | 1 | 20.567 | 27.3 | 435 | 159 | 4.35 | 3.15 | 12 | Curt-Stenvert-Bogen 15