Project Summary

Project: Project 1

| Client: | Example Company |
| --- | --- |
|  | Example street 1 |
|  | 12345 Example city |
| Created by: | Engineering office Example company |
|  | Example street 2 |
|  | 12345 Example city |

Report created by:  Test

Creation date:  09.09.2026 (13:46)

Table of contents

1 Summary	1

1.1 Scenario comparison	1

2 Supply scenarios	2

2.1 Scenario 1: Scenario 1	2

2.1.1 Buildings	2

2.1.2 Heat network	4

2.1.3 Energy hub	8

2.1.4 Economic results	11

2.2 Scenario 2: Scenario 2	15

2.2.1 Buildings	15

2.2.2 Heat network	16

2.2.3 Energy hub	20

2.2.4 Economic results	23

3 Scenario comparison	28

4 Appendix	33

4.1 Buildings	33

4.1.1 Buildings: Economic parameters	33

4.2 Heat network	35

4.2.1 Heat network: General parameters	35

4.2.2 Heat network: Pipe parameters	36

4.2.3 Heat network: Design criteria	37

4.2.4 Heat network: Fluid parameters	39

4.3 Energy hub	39

4.3.1 Energy hub: General parameters	39

4.3.2 Energy hub: Technology settings	40

4.3.3 Energy hub: Economic parameters	42

4.3.4 Energy hub: Import and feed-in	43

4.4 Economic parameters	44

4.5 Project and weather data	45

4.5.1 General project data	45

4.5.2 Weather data	45

4.6 Additional information and data sources	50

Tables

Table 1: Scenario 1: Fact sheet for the supply scenario: Scenario 1	2

Table 2: Scenario 1: Heat demands of the buildings	3

Table 3: Scenario 1: Cooling demands of the buildings	3

Table 4: Scenario 1: Electricity demands of the buildings	3

Table 5: Scenario 1: Installed building energy systems	4

Table 6: Scenario 1: Heat balance of the heat network	4

Table 7: Scenario 1: Cooling balance of the heat network	4

Table 8: Scenario 1: Electricity balance of the district	4

Table 9: Scenario 1: Properties of the heat network	5

Table 10: Scenario 1: Pump work and pressure	8

Table 11: Scenario 1: Pressure losses (critical path)	8

Table 12: Scenario 1: Sizing of the technologies in the energy hub	8

Table 17: Scenario 1: Energy import	9

Table 18: Scenario 1: Energy feed-in	10

Table 19: Scenario 1: Electricity generation and import	10

Table 20: Scenario 1: Heat generation and import	10

Table 21: Scenario 1: Emissions	10

Table 22: Scenario 1: Primary energy factor	10

Table 23: Scenario 1: Economic KPIs	11

Table 24: Scenario 1: Subsidies	11

Table 25: Scenario 1: Cost breakdown in €	11

Table 26: Scenario 2: Fact sheet for the supply scenario: Scenario 2	15

Table 27: Scenario 2: Heat demands of the buildings	15

Table 28: Scenario 2: Cooling demands of the buildings	15

Table 29: Scenario 2: Electricity demands of the buildings	16

Table 30: Scenario 2: Installed building energy systems	16

Table 31: Scenario 2: Heat balance of the heat network	16

Table 32: Scenario 2: Cooling balance of the heat network	16

Table 33: Scenario 2: Electricity balance of the district	17

Table 34: Scenario 2: Properties of the heat network	17

Table 35: Scenario 2: Pump work and pressure	20

Table 36: Scenario 2: Pressure losses (critical path)	20

Table 37: Scenario 2: Sizing of the technologies in the energy hub	20

Table 42: Scenario 2: Energy import	21

Table 43: Scenario 2: Energy feed-in	22

Table 44: Scenario 2: Electricity generation and import	22

Table 45: Scenario 2: Heat generation and import	22

Table 46: Scenario 2: Emissions	22

Table 47: Scenario 2: Primary energy factor	22

Table 48: Scenario 2: Economic KPIs	23

Table 49: Scenario 2: Subsidies	23

Table 50: Scenario 2: Cost breakdown in €	23

Table 51: Optimization of the energy hub	28

Table 52: Economic KPIs	28

Table 53: Cost breakdown in €	28

Table 54: Emissions and primary energy	32

Table 55: Cost parameters decentral technologies for scenario 'Scenario 1'	33

Table 56: Cost parameters decentral technologies for scenario 'Scenario 2'	34

Table 57: Heat network settings	35

Table 58: Hydraulic settings	36

Table 59: Pipe parameters: Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal) for scenario 'Scenario 1'	36

Table 60: Pipe parameters: Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal) for scenario 'Scenario 2'	36

Table 61: Pipe costs for all scenarios	37

Table 62: Sizing criteria: Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal) for scenario 'Scenario 1'	37

Table 63: Sizing criteria: Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal) for scenario 'Scenario 2'	37

Table 64: Fluid parameters	39

Table 65: Settings of the design optimization	39

Table 66: Settings of energy demands	39

Table 67: Ecologic parameters	40

Table 68: Emission and primary energy factors for scenario 'Scenario 1'	40

Table 69: Emission and primary energy factors for scenario 'Scenario 2'	40

Table 70: Biomass CHP 1: Settings	40

Table 71: Photovoltaics: Settings	40

Table 72: Solar thermal: Settings	41

Table 73: Geothermal probes 1: Settings	41

Table 74: Air-source heat pump: Settings	42

Table 75: Heat storage: Settings	42

Table 76: Cost parameters for scenario 'Scenario 1'	42

Table 77: Cost parameters for scenario 'Scenario 2'	43

Table 78: Electricity grid	43

Table 79: Natural gas	43

Table 80: Biomass	44

Table 81: Economic parameters	44

Table 82: Other costs: One-time costs for all scenarios	44

Table 83: Other costs: Annual costs for all scenarios	44

Table 84: Revenue settings: Components	44

Table 85: Revenue settings: Prices for all scenarios	45

Table 86: Project settings	45

Table 87: Geographical location (weather data)	45

Table 88: Customization of weather data	45

Figures

Figure 1: Specific costs and emissions	1

Figure 2: Scenario 1: Hourly total heat demand of all buildings	2

Figure 3: Scenario 1: Hourly total cooling demand of all buildings	3

Figure 4: Scenario 1: Distribution of pipe diameters	5

Figure 5: Scenario 1: Design result: Pipe Diameter and floor area of buildings	6

Figure 6: Scenario 1: Annual profile of supply and return temperature in the heat network	6

Figure 7: Scenario 1: Design result: Supply temperature and heat demand of buildings	7

Figure 8: Scenario 1: Heat flow: network to ground	7

Figure 9: Scenario 1: Diversity factor	8

Figure 10: Scenario 2: Distribution of pipe diameters	17

Figure 11: Scenario 2: Design result: Pipe Diameter and floor area of buildings	18

Figure 12: Scenario 2: Annual profile of supply and return temperature in the heat network	18

Figure 13: Scenario 2: Design result: Supply temperature and heat demand of buildings	19

Figure 14: Scenario 2: Heat flow: network to ground	19

Figure 15: Scenario 2: Diversity factor	20

Figure 16: Specific costs and emissions	31

Figure 17: Total costs and emissions	31

Figure 18: Energy import and feed-in	31

Figure 19: Energy demands	32

Figure 20: Design criteria: pressure gradient (Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal))	38

Figure 21: Design criteria: flow velocity (Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal))	39

Figure 22: Ambient air temperature (Annual profile)	46

Figure 23: Ambient air temperature (Heatmap)	46

Figure 24: Wind speed (Annual profile)	47

Figure 25: Wind speed (Heatmap)	47

Figure 26: Global horizontal irradiance (annual profile)	48

Figure 27: Global horizontal irradiance (Heatmap)	48

Figure 28: Direct normal irradiance (Annual profile)	49

Figure 29: Direct normal irradiance (Heatmap)	49

Figure 30: Horizontal infrared radiation (Annual profile)	50

Figure 31: Horizontal infrared radiation (Heatmap)	50

# 1 Summary

## 1.1 Scenario comparison

Figure 1: Specific costs and emissions

# 2 Supply scenarios

## 2.1 Scenario 1: Scenario 1

Fact sheet for the supply scenario

Table 1: Scenario 1: Fact sheet for the supply scenario: Scenario 1

| Heat network | yes |
| --- | --- |
| Buildings | 38 residential buildings, 12 non-residential buildings |
| Connected buildings | 47 |
| Installed Heatpumps in buildings | 3 |
| Heat network type | Conventional district heating network 75 °C (constant) / 55 °C (constant) |
| Technologies in energy hub | Biomass CHP 1, Photovoltaics, Solar thermal, Geothermal probes 1 |

### 2.1.1 Buildings

Figure 2: Scenario 1: Hourly total heat demand of all buildings

Figure 3: Scenario 1: Hourly total cooling demand of all buildings

Table 2: Scenario 1: Heat demands of the buildings

|  | Annual energy | Peak power |
| --- | --- | --- |
| Space heating | 623 MWh | 563 kW |
| Domestic hot water | 143 MWh |  |
| Total | 766 MWh |  |
| Heat generation of air-source heat pumps | – 39.4 MWh |  |
| Heat generation of decentral hot water heaters | – 9 MWh |  |
| Heat import of all buildings | 718 MWh | 516 kW |
| Heat losses | 164 MWh | 21.4 kW |
| Heating load at energy hub | 881 MWh | 537 kW |

Table 3: Scenario 1: Cooling demands of the buildings

|  | Annual energy | Peak power |
| --- | --- | --- |
| Space cooling | 22.4 MWh | 66 kW |
| Process cooling | 0 MWh | 0 kW |
| Total | 22.4 MWh | 66 kW |
| Cooling generation of air-cooled chillers | – 22.4 MWh |  |
| Waste heat feed-in heat network | 0 MWh | 0 kW |

Table 4: Scenario 1: Electricity demands of the buildings

|  | Annual energy | Peak power |
| --- | --- | --- |
| Plug loads | 6 MWh | 2.7 kW |
| E-mobility | 498 MWh | 153 kW |
| Total | 504 MWh | 154 kW |
| Operating power of all buildings | + 20.4 MWh |  |
| Electricity import of all buildings | 524 MWh |  |

Table 5: Scenario 1: Installed building energy systems

|  | Count | Installed capacity | Useful energy | Electricity demand | Fuel demand | SCOP |
| --- | --- | --- | --- | --- | --- | --- |
| Heat transfer station | 47 | 987 kWₜₕ | 718 MWh | --- | --- | --- |
| Air-source heat pump | 3 | 52 kWₜₕ | 39.4 MWh | 8.9 MWh | --- | 4.4 |
| El. hot water heater | 6 | 214 kWₜₕ | 9 MWh | 9 MWh | --- | --- |
| Storage (domestic hot water) | 47 | 14,100 l | --- | --- | --- | --- |
| Air chiller | 7 | 66 kWₜₕ | 22.4 MWh | 2.5 MWh | --- | 9 |

### 2.1.2 Heat network

Table 6: Scenario 1: Heat balance of the heat network

|  | Annual energy | Peak power |
| --- | --- | --- |
| Heat import of all buildings | 718 MWh | 516 kW |
| Heat losses | + 164 MWh | 21.4 kW |
| Heating load at energy hub | 881 MWh | 537 kW |

Table 7: Scenario 1: Cooling balance of the heat network

|  | Annual energy | Peak power |
| --- | --- | --- |
| Waste heat feed-in heat network | 0 MWh | 0 kW |

Table 8: Scenario 1: Electricity balance of the district

|  | Annual energy | Peak power |
| --- | --- | --- |
| Electricity import of all buildings | 524 MWh |  |
| Pump work | + 6.7 MWh | 4.9 kW |
| Electricity demand district | 531 MWh |  |

Table 9: Scenario 1: Properties of the heat network

| Network properties |  |
| --- | --- |
| Route length | 1.4 km |
| of which distribution pipes | 0.78 km |
| of which connection pipes | 0.62 km |
| Supply temperature | 75 °C (constant) |
| Return temperature | 55 °C (constant) |
| Water mass | 4.1 t |
| Water volume | 4.2 m³ |
| Linear heat density | 0.51 MWh/m |
| District area | 2.7 ha |
| Heat density | 284 MWh/ha |

Figure 4: Scenario 1: Distribution of pipe diameters

Figure 5: Scenario 1: Design result: Pipe Diameter and floor area of buildings

Figure 6: Scenario 1: Annual profile of supply and return temperature in the heat network

Figure 7: Scenario 1: Design result: Supply temperature and heat demand of buildings

Figure 8: Scenario 1: Heat flow: network to ground

Figure 9: Scenario 1: Diversity factor

Table 10: Scenario 1: Pump work and pressure

| Pump work and pressure |  |
| --- | --- |
| Mean pressure gradient | 329 Pa/m |
| Pressure loss (critical path) | 3.8 bar |
| Flow rate network pump | 34.3 m³/h |
| Max. pump power | 3.6 kW |
| Elec. power demand of pump | 4.8 kW |
| Power demand pump | 6.7 MWh |
| Relative power demand pump | 0.94 % |
| Pressure rating | PN16 |

Table 11: Scenario 1: Pressure losses (critical path)

| Pressure losses (critical path) |  |
| --- | --- |
| Pressure loss energy hub | 0.2 bar |
| Pressure loss substation | 0.3 bar |
| Pressure loss pipes | 2.7 bar |
| Pressure loss fittings / installations | 0.66 bar |
| Pressure loss (critical path) | 3.8 bar |
| Building name | Marie-Hüllenkremer-Straße 23 |

### 2.1.3 Energy hub

Table 12: Scenario 1: Sizing of the technologies in the energy hub

| Technology | Dimensioning | Full load hours/Charging cycles |
| --- | --- | --- |
| Biomass CHP 1 | 56 kWₑₗ | 4,766 h |
| Photovoltaics | 224 kWₚ | 970 h |
| Solar thermal | 1,000 m² | 76 h |
| Geothermal probes 1 | 342 kWₜₕ | 930 h |

| Nominal electric capacity | 56 kWₑₗ |
| --- | --- |
| Generated electricity | 267 MWh |
| Generated heat | 381 MWh |
| Fuel demand | 763 MWh |
| Full load hours | 4,766 h |

| Installed capacity | 224 kWₚ |
| --- | --- |
| Collector area | 1,400 m² |
| Generated electricity | 217 MWh |
| Full load hours | 970 h |
| Curtailed generation potential | 0 MWh |

| Collector area | 0 m² |
| --- | --- |
| Generated heat | 76 MWh |
| Curtailed generation potential | 179 MWh |
| Yield per collector area | 76 h |

| Extraction rate | 342 kWₜₕ |
| --- | --- |
| Generated heat | 424 MWh |
| Heat pump capacity | 456 kWₜₕ |
| Electricity demand | 106 MWh |

Table 13: Scenario 1: Energy import

|  | Annual sum | Peak power | Share |
| --- | --- | --- | --- |
| Electricity import from grid (energy hub) | 221 MWh | 177 kW | 17.3 % |
| Renewable electricity generation | 217 MWh | --- | 17.0 % |
| Biomass | 763 MWh | 160 kW | 59.7 % |
| Heat from solar thermal | 76 MWh | --- | 6.0 % |

Table 14: Scenario 1: Energy feed-in

|  | Annual energy | Peak power |
| --- | --- | --- |
| Electricity feed-in | 68 MWh | 132 kW |

Table 15: Scenario 1: Electricity generation and import

| Technology | Annual energy | Share |
| --- | --- | --- |
| Biomass CHP 1 | 267 MWh | 37.9 % |
| Renewable electricity generation | 217 MWh | 30.8 % |
| Share photovoltaics | 217 MWh | 30.8 % |
| Electricity import from grid (energy hub) | 221 MWh | 31.3 % |
|  | Self-sufficiency (autarky) rate | 65 % |
|  | Self-consumption rate | 86 % |

Table 16: Scenario 1: Heat generation and import

| Technology | Annual energy | Share |
| --- | --- | --- |
| Biomass CHP 1 | 381 MWh | 43.2 % |
| Solar thermal | 76 MWh | 8.6 % |
| Geothermal probes 1 | 424 MWh | 48.1 % |
| Solar thermal coverage rate |  | 8.6 % |

Emissions and primary energy

Table 17: Scenario 1: Emissions

|  | Spec. emissions |  | Annual sum |  | CO₂ emissions |
| --- | --- | --- | --- | --- | --- |
| Electricity import (energy hub) | 350 g/kWh | × | 221 MWh | = | 77 t |
| Electricity feed-in | - 0 g/kWh | × | 68 MWh | = | - 0 t |
| Biomass | 40 g/kWh | × | 763 MWh | = | 30.5 t |
| District heating import | 150 g/kWh | × | 0 MWh | = | 0 t |
| District cooling import | 150 g/kWh | × | 0 MWh | = | 0 t |
|  |  |  | Sum |  | 108 t |

Table 18: Scenario 1: Primary energy factor

|  | Primary energy factor |  | Annual sum |  | Primary energy |
| --- | --- | --- | --- | --- | --- |
| Electricity import (energy hub) | 1.8 | × | 221 MWh | = | 398 MWh |
| Electricity feed-in | - 0 | × | 68 MWh | = | - 0 MWh |
| Biomass | 0.2 | × | 763 MWh | = | 153 MWh |
| District heating import | 0.6 | × | 0 MWh | = | 0 MWh |
| District cooling import | 0.8 | × | 0 MWh | = | 0 MWh |
|  |  |  | Sum |  | 550 MWh |

### 2.1.4 Economic results

Summary

Table 19: Scenario 1: Economic KPIs

| Net present value | + 639,921 € |
| --- | --- |
| Amortization period | 17 years |
| Internal rate of return | 7.9 % |
| Total costs (excl. sales revenues) | 3,924,707.0 € |
| Levelized costs of energy | 0.244 €/kWh |
| Annual energy costs per floor area | 46.32 €/m² |
| Monthly energy costs per floor area | 3.86 €/m² |

Table 20: Scenario 1: Subsidies

| Initial investment | 3,612,164.0 € |
| --- | --- |
| Subsidy on initial investment | 1,203,486.0 € |
| Subsidy rate for initial investment | 33.3 % |
| Total costs (excl. all revenues and subsidies) | 5,162,090 € |
| Total subsidy in observation period | 1,253,335.0 € |
| Subsidy rate (total) | 24.3 % |

Cost and revenue details

Table 21: Scenario 1: Cost breakdown in €

|  | Sum | 2027 | 2028 | 2029 | 2030 | ... | 2046 | 2047 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Total costs | -639,921 | 2,032,678 | -176,079 | -167,694 | -159,709 | ... | -73,164 | -471,573 |
| Investment cost | 3,243,622 | 3,612,164 | 0 | 0 | 0 | ... | 0 | -401,892 |
| Building energy systems | 492,771 | 563,133 | 0 | 0 | 0 | ... | 0 | -70,362 |
| El. hot water heater | 5,590 | 5,590 | 0 | 0 | 0 | ... | 0 | 0 |
| Air-source heat pump | 82,005 | 82,005 | 0 | 0 | 0 | ... | 0 | 0 |
| Air chiller | 77,242 | 77,242 | 0 | 0 | 0 | ... | 0 | 0 |
| Storage (domestic hot water) | 65,341 | 74,730 | 0 | 0 | 0 | ... | 0 | -9,388 |
| Heat transfer station | 262,590 | 323,564 | 0 | 0 | 0 | ... | 0 | -60,974 |
| Heat network | 1,015,929 | 1,251,830 | 0 | 0 | 0 | ... | 0 | -235,900 |
| Connection pipe | 418,062 | 515,137 | 0 | 0 | 0 | ... | 0 | -97,075 |
| Distribution pipe | 597,866 | 736,692 | 0 | 0 | 0 | ... | 0 | -138,825 |
| Energy hub | 1,454,921 | 1,517,200 | 0 | 0 | 0 | ... | 0 | -95,629 |
| Biomass CHP 1 | 87,858 | 72,800 | 0 | 0 | 0 | ... | 0 | -18,291 |
| Photovoltaics | 246,400 | 246,400 | 0 | 0 | 0 | ... | 0 | 0 |
| Solar thermal | 400,000 | 400,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Geothermal probes 1 | 264,662 | 342,000 | 0 | 0 | 0 | ... | 0 | -77,337 |
| Heat pump (Geothermal probes 1) | 456,000 | 456,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Other costs | 280,000 | 280,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Gebäude Energiezentrale | 150,000 | 150,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Netzpumpe, Druckhaltung, Armaturen | 30,000 | 30,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Planungskosten | 100,000 | 100,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Maintenance costs | 532,171 | 0 | 40,669 | 38,732 | 36,888 | ... | 16,898 | 16,094 |
| Building energy systems | 80,711 | 0 | 6,168 | 5,874 | 5,594 | ... | 2,562 | 2,440 |
| El. hot water heater | 696 | 0 | 53 | 50 | 48 | ... | 22 | 21 |
| Air-source heat pump | 20,439 | 0 | 1,562 | 1,487 | 1,416 | ... | 649 | 618 |
| Air chiller | 19,252 | 0 | 1,471 | 1,401 | 1,334 | ... | 611 | 582 |
| Heat transfer station | 40,323 | 0 | 3,081 | 2,934 | 2,795 | ... | 1,280 | 1,219 |
| Heat network | 156,005 | 0 | 11,922 | 11,354 | 10,813 | ... | 4,953 | 4,718 |
| Connection pipe | 64,197 | 0 | 4,906 | 4,672 | 4,449 | ... | 2,038 | 1,941 |
| Distribution pipe | 91,808 | 0 | 7,016 | 6,682 | 6,363 | ... | 2,915 | 2,776 |
| Energy hub | 291,715 | 0 | 22,293 | 21,231 | 20,220 | ... | 9,263 | 8,822 |
| Biomass CHP 1 | 72,579 | 0 | 5,546 | 5,282 | 5,030 | ... | 2,304 | 2,195 |
| Photovoltaics | 30,706 | 0 | 2,346 | 2,234 | 2,128 | ... | 975 | 928 |
| Solar thermal | 74,773 | 0 | 5,714 | 5,442 | 5,183 | ... | 2,374 | 2,261 |
| Heat pump (Geothermal probes 1) | 113,655 | 0 | 8,685 | 8,272 | 7,878 | ... | 3,609 | 3,437 |
| Other costs | 3,738 | 0 | 285 | 272 | 259 | ... | 118 | 113 |
| Netzpumpe, Druckhaltung, Armaturen | 3,738 | 0 | 285 | 272 | 259 | ... | 118 | 113 |
| Other operation costs | 124,622 | 0 | 9,523 | 9,070 | 8,638 | ... | 3,957 | 3,768 |
| Verwaltung | 124,622 | 0 | 9,523 | 9,070 | 8,638 | ... | 3,957 | 3,768 |
| Energy costs | 1,311,523 | 0 | 100,228 | 95,455 | 90,910 | ... | 41,647 | 39,663 |
| Energy hub | 1,311,523 | 0 | 100,228 | 95,455 | 90,910 | ... | 41,647 | 39,663 |
| Electricity | 550,829 | 0 | 42,095 | 40,090 | 38,181 | ... | 17,491 | 16,658 |
| Energy charge | 550,829 | 0 | 42,095 | 40,090 | 38,181 | ... | 17,491 | 16,658 |
| Biomass | 760,693 | 0 | 58,133 | 55,365 | 52,728 | ... | 24,155 | 23,005 |
| Energy charge | 760,693 | 0 | 58,133 | 55,365 | 52,728 | ... | 24,155 | 23,005 |
| Revenues | -4,598,525 | -376,000 | -322,691 | -307,325 | -292,690 | ... | -134,085 | -127,700 |
| Feed-in | -33,897 | 0 | -2,590 | -2,467 | -2,349 | ... | -1,076 | -1,025 |
| Electricity | -33,897 | 0 | -2,590 | -2,467 | -2,349 | ... | -1,076 | -1,025 |
| Cover energy demands | -4,564,628 | -376,000 | -320,101 | -304,858 | -290,341 | ... | -133,008 | -126,674 |
| Heat demand | -2,096,628 | 0 | -160,227 | -152,597 | -145,331 | ... | -66,577 | -63,407 |
| Energy charge | -1,718,718 | 0 | -131,347 | -125,092 | -119,135 | ... | -54,577 | -51,978 |
| Capacity charge | -377,910 | 0 | -28,880 | -27,505 | -26,195 | ... | -12,000 | -11,428 |
| Cold demand | -82,890 | 0 | -6,334 | -6,032 | -5,745 | ... | -2,632 | -2,506 |
| Energy charge | -41,833 | 0 | -3,197 | -3,044 | -2,899 | ... | -1,328 | -1,265 |
| Capacity charge | -41,056 | 0 | -3,137 | -2,988 | -2,845 | ... | -1,303 | -1,241 |
| Plug loads | -24,206 | 0 | -1,849 | -1,761 | -1,677 | ... | -768 | -732 |
| Energy charge | -22,536 | 0 | -1,722 | -1,640 | -1,562 | ... | -715 | -681 |
| Capacity charge | -1,669 | 0 | -127 | -121 | -115 | ... | -53 | -50 |
| E-mobility | -1,984,902 | 0 | -151,689 | -144,465 | -137,586 | ... | -63,030 | -60,028 |
| Energy charge | -1,860,280 | 0 | -142,165 | -135,395 | -128,948 | ... | -59,072 | -56,259 |
| Capacity charge | -124,622 | 0 | -9,523 | -9,070 | -8,638 | ... | -3,957 | -3,768 |
| One-time connection fees | -376,000 | -376,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Subsidy | -1,253,335 | -1,203,486 | -3,809 | -3,628 | -3,455 | ... | -1,582 | -1,507 |
| Building energy systems | -161,553 | -161,553 | 0 | 0 | 0 | ... | 0 | 0 |
| El. hot water heater | -2,236 | -2,236 | 0 | 0 | 0 | ... | 0 | 0 |
| Storage (domestic hot water) | -29,892 | -29,892 | 0 | 0 | 0 | ... | 0 | 0 |
| Heat transfer station | -129,425 | -129,425 | 0 | 0 | 0 | ... | 0 | 0 |
| Heat network | -500,732 | -500,732 | 0 | 0 | 0 | ... | 0 | 0 |
| Connection pipe | -206,055 | -206,055 | 0 | 0 | 0 | ... | 0 | 0 |
| Distribution pipe | -294,677 | -294,677 | 0 | 0 | 0 | ... | 0 | 0 |
| Energy hub | -479,200 | -479,200 | 0 | 0 | 0 | ... | 0 | 0 |
| Solar thermal | -160,000 | -160,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Geothermal probes 1 | -136,800 | -136,800 | 0 | 0 | 0 | ... | 0 | 0 |
| Heat pump (Geothermal probes 1) | -182,400 | -182,400 | 0 | 0 | 0 | ... | 0 | 0 |
| Other costs | -62,000 | -62,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Netzpumpe, Druckhaltung, Armaturen | -12,000 | -12,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Planungskosten | -50,000 | -50,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Other operation costs | -49,848 | 0 | -3,809 | -3,628 | -3,455 | ... | -1,582 | -1,507 |
| Verwaltung | -49,848 | 0 | -3,809 | -3,628 | -3,455 | ... | -1,582 | -1,507 |

## 2.2 Scenario 2: Scenario 2

Fact sheet for the supply scenario

Table 22: Scenario 2: Fact sheet for the supply scenario: Scenario 2

| Heat network | yes |
| --- | --- |
| Buildings | 38 residential buildings, 12 non-residential buildings |
| Connected buildings | 47 |
| Installed Heatpumps in buildings | 4 |
| Installed electric hot water heaters in buildings | 1 |
| Heat network type | Conventional district heating network 75 °C (constant) / 55 °C (constant) |
| Technologies in energy hub | Gas CHP 1, Photovoltaics, Air-source heat pump, Heat storage |

### 2.2.1 Buildings

Table 23: Scenario 2: Heat demands of the buildings

|  | Annual energy | Peak power |
| --- | --- | --- |
| Space heating | 623 MWh | 563 kW |
| Domestic hot water | 143 MWh |  |
| Total | 766 MWh |  |
| Heat generation of air-source heat pumps | – 39.4 MWh |  |
| Heat generation of ground-source heat pumps | – 9.7 MWh |  |
| Heat generation of heating rods | – 3.2 MWh |  |
| Heat generation of decentral hot water heaters | – 9 MWh |  |
| Heat import of all buildings | 705 MWh | 504 kW |
| Heat losses | 253 MWh | 33.3 kW |
| Heating load at energy hub | 958 MWh | 536 kW |

Table 24: Scenario 2: Cooling demands of the buildings

|  | Annual energy | Peak power |
| --- | --- | --- |
| Space cooling | 22.4 MWh | 66 kW |
| Process cooling | 0 MWh | 0 kW |
| Total | 22.4 MWh | 66 kW |
| Cooling generation of air-cooled chillers | – 22.4 MWh |  |
| Waste heat feed-in heat network | 0 MWh | 0 kW |

Table 25: Scenario 2: Electricity demands of the buildings

|  | Annual energy | Peak power |
| --- | --- | --- |
| Plug loads | 6 MWh | 2.7 kW |
| E-mobility | 498 MWh | 153 kW |
| Total | 504 MWh | 154 kW |
| Operating power of all buildings | + 25.6 MWh |  |
| Electricity import of all buildings | 529 MWh |  |

Table 26: Scenario 2: Installed building energy systems

|  | Count | Installed capacity | Useful energy | Electricity demand | Fuel demand | SCOP |
| --- | --- | --- | --- | --- | --- | --- |
| Heat transfer station | 47 | 985 kWₜₕ | 705 MWh | --- | --- | --- |
| Ground-source heat pump | 1 | 12.8 kWₜₕ | 9.7 MWh | 2 MWh | --- | 4.9 |
| Air-source heat pump | 3 | 52 kWₜₕ | 39.4 MWh | 8.9 MWh | --- | 4.4 |
| Geothermal boreholes | 1 | 10.8 kWₜₕ | 7.7 MWh | --- | --- | --- |
| Electric heating rod | 1 | 20.9 kWₜₕ | 3.2 MWh | 3.2 MWh | --- | --- |
| El. hot water heater | 6 | 214 kWₜₕ | 9 MWh | 9 MWh | --- | --- |
| Storage (domestic hot water) | 47 | 14,100 l | --- | --- | --- | --- |
| Air chiller | 7 | 66 kWₜₕ | 22.4 MWh | 2.5 MWh | --- | 9 |

### 2.2.2 Heat network

Table 27: Scenario 2: Heat balance of the heat network

|  | Annual energy | Peak power |
| --- | --- | --- |
| Heat import of all buildings | 705 MWh | 504 kW |
| Heat losses | + 253 MWh | 33.3 kW |
| Heating load at energy hub | 958 MWh | 536 kW |

Table 28: Scenario 2: Cooling balance of the heat network

|  | Annual energy | Peak power |
| --- | --- | --- |
| Waste heat feed-in heat network | 0 MWh | 0 kW |

Table 29: Scenario 2: Electricity balance of the district

|  | Annual energy | Peak power |
| --- | --- | --- |
| Electricity import of all buildings | 529 MWh |  |
| Pump work | + 3.6 MWh | 2.6 kW |
| Electricity demand district | 533 MWh |  |

Table 30: Scenario 2: Properties of the heat network

| Network properties |  |
| --- | --- |
| Route length | 1.4 km |
| of which distribution pipes | 0.78 km |
| of which connection pipes | 0.62 km |
| Supply temperature | 75 °C (constant) |
| Return temperature | 55 °C (constant) |
| Water mass | 5.3 t |
| Water volume | 5.4 m³ |
| Linear heat density | 0.5 MWh/m |
| District area | 2.7 ha |
| Heat density | 284 MWh/ha |

Figure 10: Scenario 2: Distribution of pipe diameters

Figure 11: Scenario 2: Design result: Pipe Diameter and floor area of buildings

Figure 12: Scenario 2: Annual profile of supply and return temperature in the heat network

Figure 13: Scenario 2: Design result: Supply temperature and heat demand of buildings

Figure 14: Scenario 2: Heat flow: network to ground

Figure 15: Scenario 2: Diversity factor

Table 31: Scenario 2: Pump work and pressure

| Pump work and pressure |  |
| --- | --- |
| Mean pressure gradient | 157 Pa/m |
| Pressure loss (critical path) | 2.1 bar |
| Flow rate network pump | 33.5 m³/h |
| Max. pump power | 1.9 kW |
| Elec. power demand of pump | 2.6 kW |
| Power demand pump | 3.6 MWh |
| Relative power demand pump | 0.51 % |
| Pressure rating | PN16 |

Table 32: Scenario 2: Pressure losses (critical path)

| Pressure losses (critical path) |  |
| --- | --- |
| Pressure loss energy hub | 0.2 bar |
| Pressure loss substation | 0.3 bar |
| Pressure loss pipes | 1.3 bar |
| Pressure loss fittings / installations | 0.32 bar |
| Pressure loss (critical path) | 2.1 bar |
| Building name | Marie-Hüllenkremer-Straße 23 |

### 2.2.3 Energy hub

Table 33: Scenario 2: Sizing of the technologies in the energy hub

| Technology | Dimensioning | Full load hours/Charging cycles |
| --- | --- | --- |
| Gas CHP 1 | 139 kWₑₗ | 2,626 h |
| Photovoltaics | 251 kWₚ | 970 h |
| Air-source heat pump | 640 kWₜₕ | 687 h |
| Heat storage | 23.9 m³ | 425 |

| Nominal electric capacity | 139 kWₑₗ |
| --- | --- |
| Generated electricity | 365 MWh |
| Generated heat | 522 MWh |
| Fuel demand | 1,043 MWh |
| Full load hours | 2,626 h |

| Installed capacity | 251 kWₚ |
| --- | --- |
| Collector area | 1,569 m² |
| Generated electricity | 243 MWh |
| Full load hours | 970 h |
| Curtailed generation potential | 0 MWh |

| Generated heat | 440 MWh |
| --- | --- |
| Generated cold | 0 MWh |
| Electricity demand | 164 MWh |
| Heat for regeneration | 0 MWh |
| Full load hours | 687 h |
| Nominal heating power | 640 kWₜₕ |
| Nominal electric capacity | 160 kWₑₗ |

| Storage capacity | 555 kWh |
| --- | --- |
| Charging energy | 236 MWh |
| Discharging energy | 232 MWh |
| Storage volume | 23.9 m³ |
| Full charging cycles | 425 |

Table 34: Scenario 2: Energy import

|  | Annual sum | Peak power | Share |
| --- | --- | --- | --- |
| Electricity import from grid (energy hub) | 114 MWh | 154 kW | 8.1 % |
| Renewable electricity generation | 243 MWh | --- | 17.4 % |
| Natural gas | 1,043 MWh | 398 kW | 74.5 % |

Table 35: Scenario 2: Energy feed-in

|  | Annual energy | Peak power |
| --- | --- | --- |
| Electricity feed-in | 25.9 MWh | 131 kW |

Table 36: Scenario 2: Electricity generation and import

| Technology | Annual energy | Share |
| --- | --- | --- |
| Gas CHP 1 | 365 MWh | 50.6 % |
| Renewable electricity generation | 243 MWh | 33.7 % |
| Share photovoltaics | 243 MWh | 33.7 % |
| Electricity import from grid (energy hub) | 114 MWh | 15.8 % |
|  | Self-sufficiency (autarky) rate | 84 % |
|  | Self-consumption rate | 96 % |

Table 37: Scenario 2: Heat generation and import

| Technology | Annual energy | Share |
| --- | --- | --- |
| Gas CHP 1 | 522 MWh | 54.3 % |
| Air-source heat pump | 440 MWh | 45.7 % |

Emissions and primary energy

Table 38: Scenario 2: Emissions

|  | Spec. emissions |  | Annual sum |  | CO₂ emissions |
| --- | --- | --- | --- | --- | --- |
| Electricity import (energy hub) | 350 g/kWh | × | 114 MWh | = | 39.9 t |
| Electricity feed-in | - 0 g/kWh | × | 25.9 MWh | = | - 0 t |
| Natural gas | 250 g/kWh | × | 1,043 MWh | = | 261 t |
| District heating import | 150 g/kWh | × | 0 MWh | = | 0 t |
| District cooling import | 150 g/kWh | × | 0 MWh | = | 0 t |
|  |  |  | Sum |  | 301 t |

Table 39: Scenario 2: Primary energy factor

|  | Primary energy factor |  | Annual sum |  | Primary energy |
| --- | --- | --- | --- | --- | --- |
| Electricity import (energy hub) | 1.8 | × | 114 MWh | = | 205 MWh |
| Electricity feed-in | - 0 | × | 25.9 MWh | = | - 0 MWh |
| Natural gas | 1.1 | × | 1,043 MWh | = | 1,147 MWh |
| District heating import | 0.6 | × | 0 MWh | = | 0 MWh |
| District cooling import | 0.8 | × | 0 MWh | = | 0 MWh |
|  |  |  | Sum |  | 1,353 MWh |

### 2.2.4 Economic results

Summary

Table 40: Scenario 2: Economic KPIs

| Net present value | + 458,831 € |
| --- | --- |
| Amortization period | 19 years |
| Internal rate of return | 7.3 % |
| Total costs (excl. sales revenues) | 4,105,798.0 € |
| Levelized costs of energy | 0.255 €/kWh |
| Annual energy costs per floor area | 48.46 €/m² |
| Monthly energy costs per floor area | 4.04 €/m² |

Table 41: Scenario 2: Subsidies

| Initial investment | 3,330,428.0 € |
| --- | --- |
| Subsidy on initial investment | 1,020,584.0 € |
| Subsidy rate for initial investment | 30.6 % |
| Total costs (excl. all revenues and subsidies) | 5,139,292 € |
| Total subsidy in observation period | 1,070,433 € |
| Subsidy rate (total) | 20.8 % |

Cost and revenue details

Table 42: Scenario 2: Cost breakdown in €

|  | Sum | 2027 | 2028 | 2029 | 2030 | ... | 2046 | 2047 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Total costs | -458,830 | 1,933,844 | -161,711 | -154,011 | -146,677 | ... | -67,194 | -423,402 |
| Investment cost | 3,053,801 | 3,330,428 | 0 | 0 | 0 | ... | 0 | -359,407 |
| Building energy systems | 533,111 | 607,830 | 0 | 0 | 0 | ... | 0 | -74,718 |
| Electric heating rod | 1,153 | 1,247 | 0 | 0 | 0 | ... | 0 | -94 |
| El. hot water heater | 5,590 | 5,590 | 0 | 0 | 0 | ... | 0 | 0 |
| Ground-source heat pump | 24,671 | 24,671 | 0 | 0 | 0 | ... | 0 | 0 |
| Air-source heat pump | 82,005 | 82,005 | 0 | 0 | 0 | ... | 0 | 0 |
| Air chiller | 77,242 | 77,242 | 0 | 0 | 0 | ... | 0 | 0 |
| Storage (domestic hot water) | 65,341 | 74,730 | 0 | 0 | 0 | ... | 0 | -9,388 |
| Heat transfer station | 262,256 | 323,152 | 0 | 0 | 0 | ... | 0 | -60,896 |
| Geothermal boreholes | 14,850 | 19,189 | 0 | 0 | 0 | ... | 0 | -4,339 |
| Heat network | 1,030,511 | 1,269,798 | 0 | 0 | 0 | ... | 0 | -239,286 |
| Connection pipe | 418,062 | 515,137 | 0 | 0 | 0 | ... | 0 | -97,075 |
| Distribution pipe | 612,448 | 754,660 | 0 | 0 | 0 | ... | 0 | -142,211 |
| Energy hub | 1,210,178 | 1,172,800 | 0 | 0 | 0 | ... | 0 | -45,402 |
| Gas CHP 1 | 218,078 | 180,700 | 0 | 0 | 0 | ... | 0 | -45,402 |
| Photovoltaics | 276,100 | 276,100 | 0 | 0 | 0 | ... | 0 | 0 |
| Air-source heat pump | 704,000 | 704,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Heat storage | 12,000 | 12,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Other costs | 280,000 | 280,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Gebäude Energiezentrale | 150,000 | 150,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Netzpumpe, Druckhaltung, Armaturen | 30,000 | 30,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Planungskosten | 100,000 | 100,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Maintenance costs | 686,732 | 0 | 52,481 | 49,982 | 47,601 | ... | 21,806 | 20,768 |
| Building energy systems | 89,356 | 0 | 6,828 | 6,503 | 6,193 | ... | 2,837 | 2,702 |
| Electric heating rod | 155 | 0 | 11 | 11 | 10 | ... | 4 | 4 |
| El. hot water heater | 696 | 0 | 53 | 50 | 48 | ... | 22 | 21 |
| Ground-source heat pump | 6,149 | 0 | 469 | 447 | 426 | ... | 195 | 185 |
| Air-source heat pump | 20,439 | 0 | 1,562 | 1,487 | 1,416 | ... | 649 | 618 |
| Air chiller | 19,252 | 0 | 1,471 | 1,401 | 1,334 | ... | 611 | 582 |
| Heat transfer station | 40,271 | 0 | 3,077 | 2,931 | 2,791 | ... | 1,278 | 1,217 |
| Geothermal boreholes | 2,391 | 0 | 182 | 174 | 165 | ... | 75 | 72 |
| Heat network | 158,244 | 0 | 12,093 | 11,517 | 10,968 | ... | 5,025 | 4,785 |
| Connection pipe | 64,197 | 0 | 4,906 | 4,672 | 4,449 | ... | 2,038 | 1,941 |
| Distribution pipe | 94,047 | 0 | 7,187 | 6,844 | 6,519 | ... | 2,986 | 2,844 |
| Energy hub | 435,392 | 0 | 33,273 | 31,688 | 30,179 | ... | 13,825 | 13,167 |
| Gas CHP 1 | 180,153 | 0 | 13,767 | 13,112 | 12,487 | ... | 5,720 | 5,448 |
| Photovoltaics | 34,408 | 0 | 2,629 | 2,504 | 2,385 | ... | 1,092 | 1,040 |
| Air-source heat pump | 219,334 | 0 | 16,761 | 15,963 | 15,203 | ... | 6,964 | 6,633 |
| Heat storage | 1,495 | 0 | 114 | 108 | 103 | ... | 47 | 45 |
| Other costs | 3,738 | 0 | 285 | 272 | 259 | ... | 118 | 113 |
| Netzpumpe, Druckhaltung, Armaturen | 3,738 | 0 | 285 | 272 | 259 | ... | 118 | 113 |
| Other operation costs | 124,622 | 0 | 9,523 | 9,070 | 8,638 | ... | 3,957 | 3,768 |
| Verwaltung | 124,622 | 0 | 9,523 | 9,070 | 8,638 | ... | 3,957 | 3,768 |
| Energy costs | 1,323,985 | 0 | 101,180 | 96,362 | 91,774 | ... | 42,042 | 40,040 |
| Energy hub | 1,323,985 | 0 | 101,180 | 96,362 | 91,774 | ... | 42,042 | 40,040 |
| Electricity | 284,138 | 0 | 21,714 | 20,680 | 19,695 | ... | 9,022 | 8,593 |
| Energy charge | 284,138 | 0 | 21,714 | 20,680 | 19,695 | ... | 9,022 | 8,593 |
| Gas | 1,039,846 | 0 | 79,466 | 75,682 | 72,078 | ... | 33,020 | 31,447 |
| Energy charge | 1,039,846 | 0 | 79,466 | 75,682 | 72,078 | ... | 33,020 | 31,447 |
| Revenues | -4,577,538 | -376,000 | -321,087 | -305,798 | -291,236 | ... | -133,418 | -127,065 |
| Feed-in | -12,910 | 0 | -986 | -939 | -894 | ... | -409 | -390 |
| Electricity | -12,910 | 0 | -986 | -939 | -894 | ... | -409 | -390 |
| Cover energy demands | -4,564,628 | -376,000 | -320,101 | -304,858 | -290,341 | ... | -133,008 | -126,674 |
| Heat demand | -2,096,628 | 0 | -160,227 | -152,597 | -145,331 | ... | -66,577 | -63,407 |
| Energy charge | -1,718,718 | 0 | -131,347 | -125,092 | -119,135 | ... | -54,577 | -51,978 |
| Capacity charge | -377,910 | 0 | -28,880 | -27,505 | -26,195 | ... | -12,000 | -11,428 |
| Cold demand | -82,890 | 0 | -6,334 | -6,032 | -5,745 | ... | -2,632 | -2,506 |
| Energy charge | -41,833 | 0 | -3,197 | -3,044 | -2,899 | ... | -1,328 | -1,265 |
| Capacity charge | -41,056 | 0 | -3,137 | -2,988 | -2,845 | ... | -1,303 | -1,241 |
| Plug loads | -24,206 | 0 | -1,849 | -1,761 | -1,677 | ... | -768 | -732 |
| Energy charge | -22,536 | 0 | -1,722 | -1,640 | -1,562 | ... | -715 | -681 |
| Capacity charge | -1,669 | 0 | -127 | -121 | -115 | ... | -53 | -50 |
| E-mobility | -1,984,902 | 0 | -151,689 | -144,465 | -137,586 | ... | -63,030 | -60,028 |
| Energy charge | -1,860,280 | 0 | -142,165 | -135,395 | -128,948 | ... | -59,072 | -56,259 |
| Capacity charge | -124,622 | 0 | -9,523 | -9,070 | -8,638 | ... | -3,957 | -3,768 |
| One-time connection fees | -376,000 | -376,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Subsidy | -1,070,433 | -1,020,584 | -3,809 | -3,628 | -3,455 | ... | -1,582 | -1,507 |
| Building energy systems | -169,064 | -169,064 | 0 | 0 | 0 | ... | 0 | 0 |
| El. hot water heater | -2,236 | -2,236 | 0 | 0 | 0 | ... | 0 | 0 |
| Storage (domestic hot water) | -29,892 | -29,892 | 0 | 0 | 0 | ... | 0 | 0 |
| Heat transfer station | -129,261 | -129,261 | 0 | 0 | 0 | ... | 0 | 0 |
| Geothermal boreholes | -7,675 | -7,675 | 0 | 0 | 0 | ... | 0 | 0 |
| Heat network | -507,919 | -507,919 | 0 | 0 | 0 | ... | 0 | 0 |
| Connection pipe | -206,055 | -206,055 | 0 | 0 | 0 | ... | 0 | 0 |
| Distribution pipe | -301,864 | -301,864 | 0 | 0 | 0 | ... | 0 | 0 |
| Energy hub | -281,600 | -281,600 | 0 | 0 | 0 | ... | 0 | 0 |
| Air-source heat pump | -281,600 | -281,600 | 0 | 0 | 0 | ... | 0 | 0 |
| Other costs | -62,000 | -62,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Netzpumpe, Druckhaltung, Armaturen | -12,000 | -12,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Planungskosten | -50,000 | -50,000 | 0 | 0 | 0 | ... | 0 | 0 |
| Other operation costs | -49,848 | 0 | -3,809 | -3,628 | -3,455 | ... | -1,582 | -1,507 |
| Verwaltung | -49,848 | 0 | -3,809 | -3,628 | -3,455 | ... | -1,582 | -1,507 |

# 3 Scenario comparison

Table 43: Optimization of the energy hub

|  | Scenario 1 | Scenario 2 |
| --- | --- | --- |
| CHP 1 | 56 kWₑₗ | 139 kWₑₗ |
| Photovoltaics | 224 kWₚ | 251 kWₚ |
| Solar thermal | 1,000 m² | --- |
| Geothermal energy 1 | 342 kWₜₕ | --- |
| Air-source heat pump | --- | 160 kWₑₗ |
| Heat storage | --- | 555 kWh |

Table 44: Economic KPIs

|  | Scenario 1 | Scenario 2 |
| --- | --- | --- |
| Net present value | 639,921 € | 458,831 € |
| Amortization period | 17 years | 19 years |
| Internal rate of return | 7.9 % | 7.3 % |
| Levelized costs of heat | 0.411 €/kWh | 0.43 €/kWh |
| Levelized costs of energy | 0.244 €/kWh | 0.255 €/kWh |
| Annual energy costs per floor area | 46.3 €/m² | 48.5 €/m² |
| Monthly energy costs per floor area | 3.9 €/m² | 4 €/m² |

Table 45: Cost breakdown in €

|  | Scenario 1 | Scenario 2 |
| --- | --- | --- |
| Total costs | 639,921 | 458,831 |
| Investment cost | -3,243,622 | -3,053,802 |
| Building energy systems | -492,771 | -533,112 |
| Electric heating rod | --- | -1,154 |
| El. hot water heater | -5,590 | -5,590 |
| Ground-source heat pump | --- | -24,671 |
| Air-source heat pump | -82,006 | -82,006 |
| Air chiller | -77,243 | -77,243 |
| Storage (domestic hot water) | -65,342 | -65,342 |
| Heat transfer station | -262,591 | -262,256 |
| Geothermal boreholes | --- | -14,850 |
| Heat network | -1,015,930 | -1,030,511 |
| Connection pipe | -418,063 | -418,063 |
| Distribution pipe | -597,867 | -612,449 |
| Energy hub | -1,454,921 | -1,210,178 |
| Biomass CHP 1 | -87,859 | -218,078 |
| Photovoltaics | -246,400 | -276,100 |
| Solar thermal | -400,000 | --- |
| Geothermal probes 1 | -264,662 | --- |
| Air-source heat pump | --- | -704,000 |
| Heat storage | --- | -12,000 |
| Heat pump (Geothermal probes 1) | -456,000 | --- |
| Other costs | -280,000 | -280,000 |
| Maintenance costs | -532,172 | -686,732 |
| Building energy systems | -80,712 | -89,357 |
| Electric heating rod | --- | -155 |
| El. hot water heater | -697 | -697 |
| Ground-source heat pump | --- | -6,149 |
| Air-source heat pump | -20,440 | -20,440 |
| Air chiller | -19,252 | -19,252 |
| Heat transfer station | -40,323 | -40,272 |
| Geothermal boreholes | --- | -2,391 |
| Heat network | -156,006 | -158,245 |
| Connection pipe | -64,198 | -64,198 |
| Distribution pipe | -91,808 | -94,047 |
| Energy hub | -291,715 | -435,392 |
| Biomass CHP 1 | -72,580 | -180,154 |
| Photovoltaics | -30,707 | -34,408 |
| Solar thermal | -74,773 | --- |
| Air-source heat pump | --- | -219,335 |
| Heat storage | --- | -1,495 |
| Heat pump (Geothermal probes 1) | -113,655 | --- |
| Other costs | -3,739 | -3,739 |
| Other operation costs | -124,622 | -124,622 |
| Energy costs | -1,311,523 | -1,323,985 |
| Energy hub | -1,311,523 | -1,323,985 |
| Electricity | -550,830 | -284,138 |
| Energy charge | -550,830 | -284,138 |
| Gas | --- | -1,039,847 |
| Energy charge | --- | -1,039,847 |
| Biomass | -760,693 | --- |
| Energy charge | -760,693 | --- |
| Revenues | 4,598,525 | 4,577,538 |
| Feed-in | 33,897 | 12,911 |
| Electricity | 33,897 | 12,911 |
| Cover energy demands | 4,564,628 | 4,564,628 |
| Heat demand | 2,096,628 | 2,096,628 |
| Energy charge | 1,718,718 | 1,718,718 |
| Capacity charge | 377,910 | 377,910 |
| Cold demand | 82,891 | 82,891 |
| Energy charge | 41,834 | 41,834 |
| Capacity charge | 41,057 | 41,057 |
| Plug loads | 24,207 | 24,207 |
| Energy charge | 22,537 | 22,537 |
| Capacity charge | 1,670 | 1,670 |
| E-mobility | 1,984,902 | 1,984,902 |
| Energy charge | 1,860,280 | 1,860,280 |
| Capacity charge | 124,622 | 124,622 |
| One-time connection fees | 376,000 | 376,000 |
| Subsidy | 1,253,335 | 1,070,433 |
| Building energy systems | 161,554 | 169,065 |
| El. hot water heater | 2,236 | 2,236 |
| Storage (domestic hot water) | 29,892 | 29,892 |
| Heat transfer station | 129,426 | 129,261 |
| Geothermal boreholes | --- | 7,676 |
| Heat network | 500,732 | 507,919 |
| Connection pipe | 206,055 | 206,055 |
| Distribution pipe | 294,677 | 301,864 |
| Energy hub | 479,200 | 281,600 |
| Solar thermal | 160,000 | --- |
| Geothermal probes 1 | 136,800 | --- |
| Air-source heat pump | --- | 281,600 |
| Heat pump (Geothermal probes 1) | 182,400 | --- |
| Other costs | 62,000 | 62,000 |
| Other operation costs | 49,849 | 49,849 |

Figure 16: Specific costs and emissions

Figure 17: Total costs and emissions

Figure 18: Energy import and feed-in

Figure 19: Energy demands

Table 46: Emissions and primary energy

|  | Scenario 1 | Scenario 2 |
| --- | --- | --- |
| CO₂ emissions | 108 t | 301 t |
| CO₂ emissions per heat demand | 141 g/kWh | 392 g/kWh |
| CO₂ emissions per energy demand | 83 g/kWh | 233 g/kWh |
| CO₂ emissions per floor area | 15.9 kg/m² | 44.2 kg/m² |
| Primary energy | 550 MWh | 1,353 MWh |
| Primary energy per heat demand | 0.72 kWh/kWh | 1.8 kWh/kWh |
| Primary energy per energy demand | 0.43 kWh/kWh | 1 kWh/kWh |
| Primary energy per floor area | 81 kWh/m² | 199 kWh/m² |

# 4 Appendix

Economic evaluation and scenario comparison

## 4.1 Buildings

### 4.1.1 Buildings: Economic parameters

Table 47: Cost parameters decentral technologies for scenario 'Scenario 1'

|  | Specific investment costs (cost data points) | Lifetime | Annual maintenance costs | Subsidy |
| --- | --- | --- | --- | --- |
| Electric heating rod (domestic hot water) | 5 kW: 80 €/kW 10 kW: 50 €/kW 20 kW: 35 €/kW 50 kW: 18 €/kW | 20 years | 1 % of investment | 40 % |
| Air-source heat pump | 5 kW: 2300 €/kW 10 kW: 1800 €/kW 20 kW: 1500 €/kW 30 kW: 1400 €/kW 40 kW: 1300 €/kW 50 kW: 1200 €/kW 60 kW: 1200 €/kW 80 kW: 1200 €/kW 110 kW: 1200 €/kW | 20 years | 2 % of investment | 0 % |
| Air chiller | 5 kW: 1300 €/kW 20 kW: 900 €/kW 100 kW: 700 €/kW 250 kW: 600 €/kW 500 kW: 450 €/kW | 20 years | 2 % of investment | 0 % |
| Storage (domestic hot water) | 130 l: 8 €/l 150 l: 7 €/l 300 l: 5.3 €/l 500 l: 4.8 €/l 1000 l: 4.5 €/l | 30 years | 0 % of investment | 40 % |
| Heat transfer station | 15 kW: 380 €/kW 30 kW: 250 €/kW 100 kW: 150 €/kW 500 kW: 85 €/kW 2000 kW: 55 €/kW 10000 kW: 34 €/kW | 40 years | 1 % of investment | 40 % |

Table 48: Cost parameters decentral technologies for scenario 'Scenario 2'

|  | Specific investment costs (cost data points) | Lifetime | Annual maintenance costs | Subsidy |
| --- | --- | --- | --- | --- |
| Electric heating rod | 2 kW: 200 €/kW 5 kW: 100 €/kW 10 kW: 75 €/kW 20 kW: 60 €/kW 50 kW: 50 €/kW 100 kW: 40 €/kW | 25 years | 1 % of investment | 0 % |
| Electric heating rod (domestic hot water) | 5 kW: 80 €/kW 10 kW: 50 €/kW 20 kW: 35 €/kW 50 kW: 18 €/kW | 20 years | 1 % of investment | 40 % |
| Ground-source heat pump | 5 kW: 3000 €/kW 10 kW: 2100 €/kW 20 kW: 1500 €/kW 30 kW: 1200 €/kW 40 kW: 1100 €/kW 50 kW: 1000 €/kW 60 kW: 900 €/kW 80 kW: 800 €/kW 110 kW: 700 €/kW | 20 years | 2 % of investment | 0 % |
| Air-source heat pump | 5 kW: 2300 €/kW 10 kW: 1800 €/kW 20 kW: 1500 €/kW 30 kW: 1400 €/kW 40 kW: 1300 €/kW 50 kW: 1200 €/kW 60 kW: 1200 €/kW 80 kW: 1200 €/kW 110 kW: 1200 €/kW | 20 years | 2 % of investment | 0 % |
| Air chiller | 5 kW: 1300 €/kW 20 kW: 900 €/kW 100 kW: 700 €/kW 250 kW: 600 €/kW 500 kW: 450 €/kW | 20 years | 2 % of investment | 0 % |
| Storage (domestic hot water) | 130 l: 8 €/l 150 l: 7 €/l 300 l: 5.3 €/l 500 l: 4.8 €/l 1000 l: 4.5 €/l | 30 years | 0 % of investment | 40 % |
| Heat transfer station | 15 kW: 380 €/kW 30 kW: 250 €/kW 100 kW: 150 €/kW 500 kW: 85 €/kW 2000 kW: 55 €/kW 10000 kW: 34 €/kW | 40 years | 1 % of investment | 40 % |
| Geothermal boreholes | 5 kW: 2500 €/kW 10 kW: 1800 €/kW 20 kW: 1500 €/kW 40 kW: 1400 €/kW 60 kW: 1300 €/kW 80 kW: 1300 €/kW 110 kW: 1200 €/kW | 50 years | 1 % of investment | 40 % |

## 4.2 Heat network

### 4.2.1 Heat network: General parameters

Table 49: Heat network settings

|  | All scenarios |
| --- | --- |
| Consider heat losses | yes |
| Surcharge (fittings, etc.) | 20 % |
| Network temperature | constant |
| Design criteria | Pressure gradient and flow velocity |
| Diversity factor (method) | Neglect diversity (f=1) |
| Diversity factor only for residential buildings | no |
| Diversity factor DHW: calculation method | TU Dresden |
| Heat carrier fluid | Water |
| Thermal conductivity | 1.5 W/mK |
| Ground temperature: Option | calculated |
| Depth | 1 m |

Table 50: Hydraulic settings

|  | All scenarios |
| --- | --- |
| Circulation pump | Central pump |
| Pressure in pressure maintenance | 3 bar |
| Pressure loss fittings | 25 % |
| Pressure loss substations | 0.3 bar |
| Pressure loss energy hub: Option | fixed |
| Pressure loss energy hub | 0.2 bar |
| Waste heat feed-in | Return to supply |
| Temperature difference | 20 K |

### 4.2.2 Heat network: Pipe parameters

Table 51: Pipe parameters: Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal) for scenario 'Scenario 1'

| Nominal diameter | Outer diameter (pipe) | Thickness (pipe) | Outer diameter (case) | Thickness (case) | Installation depth | Pipe distance | Thermal conductivity (insulation) | Roughness |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DN | mm | mm | mm | mm | m | mm | W/mK | mm |
| 20 | 25 | 2.3 | 93 | 2.1 | 1.2 | 33 | 0.02 | 0.007 |
| 25 | 32 | 2.9 | 113 | 2.3 | 1.2 | 40 | 0.02 | 0.007 |
| 32 | 40 | 3.7 | 128 | 2.7 | 1.2 | 50 | 0.02 | 0.007 |
| 40 | 50 | 4.6 | 163 | 3.2 | 1.2 | 60 | 0.02 | 0.007 |
| 50 | 63 | 5.8 | 183 | 3.3 | 1.2 | 73 | 0.02 | 0.007 |
| 65 | 75 | 6.8 | 202 | 3.3 | 1.2 | 85 | 0.02 | 0.007 |

Table 52: Pipe parameters: Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal) for scenario 'Scenario 2'

| Nominal diameter | Outer diameter (pipe) | Thickness (pipe) | Outer diameter (case) | Thickness (case) | Installation depth | Pipe distance | Thermal conductivity (insulation) | Roughness |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DN | mm | mm | mm | mm | m | mm | W/mK | mm |
| 20 | 25 | 2.3 | 78 | 1.9 | 1.2 | 228 | 0.02 | 0.007 |
| 25 | 32 | 2.9 | 78 | 1.9 | 1.2 | 228 | 0.02 | 0.007 |
| 32 | 40 | 3.7 | 93 | 2.1 | 1.2 | 243 | 0.02 | 0.007 |
| 40 | 50 | 4.6 | 113 | 2.3 | 1.2 | 263 | 0.02 | 0.007 |
| 50 | 63 | 5.8 | 128 | 2.7 | 1.2 | 278 | 0.02 | 0.007 |
| 65 | 75 | 6.8 | 143 | 2.9 | 1.2 | 293 | 0.02 | 0.007 |
| 80 | 90 | 8.2 | 163 | 3.2 | 1.2 | 313 | 0.02 | 0.007 |
| 100 | 110 | 10 | 183 | 3.3 | 1.2 | 333 | 0.02 | 0.007 |
| 125 | 140 | 12.7 | 202 | 3.3 | 1.2 | 352 | 0.02 | 0.007 |
| 150 | 160 | 14.6 | 250 | 3.9 | 1.2 | 500 | 0.02 | 0.007 |

Table 53: Pipe costs for all scenarios

| Nominal diameter | Pipe cost | Installation | Total |
| --- | --- | --- | --- |
| mm | €/m | €/m | €/m |
| 32 | 79 | 740 | 819 |
| 50 | 96 | 830 | 926 |
| 80 | 130 | 970 | 1,100 |
| 100 | 160 | 1,100 | 1,260 |
| 150 | 230 | 1,300 | 1,530 |
| 200 | 320 | 1,500 | 1,820 |
| 300 | 560 | 1,800 | 2,360 |
| 400 | 860 | 2,100 | 2,960 |
| 500 | 1,200 | 2,300 | 3,500 |
| 600 | 1,600 | 2,500 | 4,100 |
| 800 | 2,700 | 2,600 | 5,300 |

### 4.2.3 Heat network: Design criteria

Table 54: Sizing criteria: Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal) for scenario 'Scenario 1'

| Nominal diameter | Max. pressure gradient | Max. flow velocity |
| --- | --- | --- |
| DN | Pa/m | m/s |
| 20 | 200 | 0.9 |
| 25 | 200 | 0.9 |
| 32 | 200 | 0.93 |
| 40 | 200 | 0.98 |
| 50 | 200 | 1 |
| 65 | 200 | 1.1 |

Table 55: Sizing criteria: Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal) for scenario 'Scenario 2'

| Nominal diameter | Max. pressure gradient | Max. flow velocity |
| --- | --- | --- |
| DN | Pa/m | m/s |
| 20 | 200 | 0.9 |
| 25 | 200 | 0.9 |
| 32 | 200 | 0.93 |
| 40 | 200 | 0.98 |
| 50 | 200 | 1 |
| 65 | 200 | 1.1 |
| 80 | 200 | 1.2 |
| 100 | 200 | 1.4 |
| 125 | 200 | 1.6 |
| 150 | 200 | 1.9 |

Figure 20: Design criteria: pressure gradient (Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal))

Figure 21: Design criteria: flow velocity (Kunststoff (Doppelrohr): BruggPipes: CALPEX DUO (normal))

### 4.2.4 Heat network: Fluid parameters

Table 56: Fluid parameters

|  | All scenarios |
| --- | --- |
| Heat carrier fluid | Water |
| Density | 981 kg/m³ |
| Viscosity | 0.0004 Pa/s |
| Specific heat capacity | 4.187 kJ/kgK |

## 4.3 Energy hub

### 4.3.1 Energy hub: General parameters

Table 57: Settings of the design optimization

|  | All scenarios |
| --- | --- |
| Optimization objective | Net present value / total annualized costs |
| Consider renewables to cover peak loads | yes |
| Conservative system design | yes |
| Set number of design days | no |
| Set time limit for calculation | no |

Table 58: Settings of energy demands

|  | All scenarios |
| --- | --- |
| Split into high- and low-temperature heat demand | no |
| Plug loads demand covered by energy hub | yes |
| Electricity for e-mobility covered by energy hub | yes |
| Electricity for building energy systems covered by energy hub | yes |
| Electricity for pumps covered by energy hub | yes |
| Hydrogen demand profile uploaded | no |

Table 59: Ecologic parameters

|  | All scenarios |
| --- | --- |
| Limit CO₂ emissions | no |
| Limit primary energy consumption | no |

Table 60: Emission and primary energy factors for scenario 'Scenario 1'

|  | CO₂ emissions | Primary energy factor |
| --- | --- | --- |
| Electricity import | 350 g/kWh | 1.8 |
| Electricity feed-in | 0 g/kWh | 0 |
| Biomass import | 40 g/kWh | 0.2 |

Table 61: Emission and primary energy factors for scenario 'Scenario 2'

|  | CO₂ emissions | Primary energy factor |
| --- | --- | --- |
| Electricity import | 350 g/kWh | 1.8 |
| Electricity feed-in | 0 g/kWh | 0 |
| Natural gas import | 250 g/kWh | 1.1 |

### 4.3.2 Energy hub: Technology settings

Table 62: Biomass CHP 1: Settings

|  | Scenario 1 | Scenario 2 |
| --- | --- | --- |
| Enabled | yes | yes |
| Define optimization interval | no | no |
| Generates high-temp. heat | no | no |
| Generates low-temp. heat | yes | yes |
| Electrical efficiency | 35 % | 35 % |
| Thermal efficiency | 50 % | 50 % |
| Fuel type | Biomass | Natural Gas |
| Direct electricity feed-in | no | no |

Table 63: Photovoltaics: Settings

|  | All scenarios |
| --- | --- |
| Enabled | yes |
| Lower area capacity limit | 0 m² |
| Upper area capacity limit | 62,500 m² |
| Lower power capacity limit | 0 kWₚ |
| Upper power capacity limit | 10,000 kWₚ |
| Area concurrence with solar thermal | no |
| Tilt angle | 30 ° |
| East-west orientation (azimuth) | 0 ° |
| Inverter efficiency | 96 % |
| System losses | 14 % |
| PV module type | Polycrystalline |
| Module efficiency | 16 % |
| Temperature coefficient | 0.42 %/°C |
| Set electricity price | no |
| Electricity generation constraint | no |

Table 64: Solar thermal: Settings

|  | Scenario 1 | Scenario 2 |
| --- | --- | --- |
| Enabled | yes | no |
| Lower limit | 1,000 m² | --- |
| Upper limit | 10,000 m² | --- |
| Area concurrence with PV | no | --- |
| Tilt angle | 30 ° | --- |
| East-west orientation (azimuth) | 0 ° | --- |
| Mean collector temperature | 80 °C | --- |
| Collector type | Flat-plate collector | --- |

Table 65: Geothermal probes 1: Settings

|  | Scenario 1 | Scenario 2 |
| --- | --- | --- |
| Enabled | yes | no |
| Geothermal technology | Geothermal probes | --- |
| Extraction temperature | 10 °C | --- |
| Define optimization interval | no | --- |
| Can generate heat | yes | --- |
| Can generate cold | no | --- |
| Generates high-temp. heat | no | --- |
| Generates low-temp. heat | yes | --- |
| Limit heat extraction | no | --- |
| Install heat pump (High temp.) | no | --- |
| Install heat pump | yes | --- |
| Heat: COP settings | Constant value | --- |
| Heat: Constant COP value | 4 | --- |
| Define heat pump capacity | no | --- |
| Limit cool extraction | no | --- |
| Install chiller | no | --- |
| Enforce regeneration | no | --- |

Table 66: Air-source heat pump: Settings

|  | Scenario 1 | Scenario 2 |
| --- | --- | --- |
| Enabled | no | yes |
| Define optimization interval | --- | no |
| Nominal COP | --- | 4 |
| Can generate heat | --- | yes |
| Can generate cold | --- | yes |
| Generates high-temp. heat | --- | no |
| Generates low-temp. heat | --- | yes |
| Use heat for regeneration | --- | no |
| HT heat: COP settings | --- | Calculate COP (Carnot) |
| HT heat: Carnot efficiency | --- | Medium efficiency (50 %) |
| HT heat: Maximum COP | --- | 6 |
| Heat: COP settings | --- | Calculate COP (Carnot) |
| Heat: Carnot efficiency | --- | Medium efficiency (50 %) |
| Heat: Maximum COP | --- | 6 |
| Cooling: COP settings | --- | Calculate COP (Carnot) |
| Cooling: Carnot efficiency | --- | Medium efficiency (50 %) |
| Cooling: Maximum COP | --- | 6 |

Table 67: Heat storage: Settings

|  | Scenario 1 | Scenario 2 |
| --- | --- | --- |
| Enabled | no | yes |
| Define optimization interval | --- | no |
| Long term storage possible | --- | no |
| Stand-by-losses | --- | 20 % per 5days |
| Temperature range | --- | 20 K |
| Limit state of charge | --- | no |
| Limit charging time/power | --- | no |

### 4.3.3 Energy hub: Economic parameters

Table 68: Cost parameters for scenario 'Scenario 1'

|  | Specific investment costs | Lifetime | Annual maintenance costs | Subsidy | Existing with remaining lifetime |
| --- | --- | --- | --- | --- | --- |
| Biomass CHP 1 | 1,300 €/kWₑₗ | 15 years | 8 % of investment | 0 % | --- |
| Photovoltaics | 1,100 €/kWₚ | 20 years | 1 % of investment | 0 % | --- |
| Solar thermal | 400 €/m² | 20 years | 1.5 % of investment | 40 % | --- |
| Geothermal probes 1 | 1,000 €/kWₜₕ | 50 years | 0 % of investment | 40 % | --- |
| Heat pump (Geothermal probes 1) | 1,000 €/kWₜₕ | 20 years | 2 % of investment | 40 % | --- |

Table 69: Cost parameters for scenario 'Scenario 2'

|  | Specific investment costs | Lifetime | Annual maintenance costs | Subsidy | Existing with remaining lifetime |
| --- | --- | --- | --- | --- | --- |
| Gas CHP 1 | 1,300 €/kWₑₗ | 15 years | 8 % of investment | 0 % | --- |
| Photovoltaics | 1,100 €/kWₚ | 20 years | 1 % of investment | 0 % | --- |
| Air-source heat pump | 1,100 €/kWₜₕ | 20 years | 2.5 % of investment | 40 % | --- |
| Heat storage | 500 €/m³ | 20 years | 1 % of investment | 0 % | --- |

### 4.3.4 Energy hub: Import and feed-in

Table 70: Electricity grid

|  | All scenarios |
| --- | --- |
| Electricity import (energy hub) | yes |
| Supply price | 0.2 €/kWh |
| Limit annual import | no |
| Annual price increase (option) | No change |
| Electricity feed-in | yes |
| Feed-in tariff | 0.04 €/kWh |
| Limit annual feed-in | no |
| Limit grid capacity | no |
| Grid capacity | no |

Table 71: Natural gas

|  | Scenario 1 | Scenario 2 |
| --- | --- | --- |
| Natural gas import | no | yes |
| Supply price | --- | 0.08 €/kWh |
| Limit annual import | --- | no |
| Annual price increase (option) | --- | No change |
| Limit grid capacity | --- | no |
| Grid capacity | --- | no |

Table 72: Biomass

|  | Scenario 1 | Scenario 2 |
| --- | --- | --- |
| Biomass import | yes | no |
| Supply price | 0.08 €/kWh | --- |
| Limit annual import | no | --- |
| Annual price increase (option) | No change | --- |

## 4.4 Economic parameters

Table 73: Economic parameters

|  | All scenarios |
| --- | --- |
| Imputed interest | 5 % |
| Observation period | 20 years |
| Year 1 of observation period | 2027 |
| Inflation rate | 0 % |
| Operating cost subsidy (BEW) of large-scale heat pumps | no |
| Operating cost subsidy (BEW) of solar thermal collectors | no |
| CO₂ price option | No pricing |

Table 74: Other costs: One-time costs for all scenarios

|  | Specific investment costs | Lifetime | Maintenance costs | Subsidy |
| --- | --- | --- | --- | --- |
| Gebäude Energiezentrale | 150,000 € | 20 years | 0 % | 0 % |
| Netzpumpe, Druckhaltung, Armaturen | 30,000 € | 20 years | 1 % | 40 % |
| Planungskosten | 100,000 € | 20 years | 0 % | 50 % |

Table 75: Other costs: Annual costs for all scenarios

|  | Annual costs | Subsidy |
| --- | --- | --- |
| Verwaltung | 10,000 € | 40 % |

Table 76: Revenue settings: Components

|  | All scenarios |
| --- | --- |
| Energy price | yes |
| Capacity price | yes |
| Base price | no |
| One-time connection fee | yes |

Table 77: Revenue settings: Prices for all scenarios

|  | Supply price | Capacity price | Heat network connection |
| --- | --- | --- | --- |
| One-time connection fees | --- | --- | 8,000 € |
| Heat demand | 0.18 €/kWh | 50 €/kW | --- |
| Cooling demand | 0.15 €/kWh | 50 €/kW | --- |
| Plug loads | 0.3 €/kWh | 50 €/kW | --- |
| E-mobility | 0.3 €/kWh | 50 €/kW | --- |

## 4.5 Project and weather data

### 4.5.1 General project data

Table 78: Project settings

|  | All scenarios |
| --- | --- |
| Min. temp. diff. water/water | 2 |
| Public holidays | yes |
| Time change | no |
| First day of year | Monday |
| Version of simulation core | 4.6 |

Table 79: Geographical location (weather data)

|  | All scenarios |
| --- | --- |
| City | Düsseldorf |
| Country | Germany |

### 4.5.2 Weather data

Table 80: Customization of weather data

|  | All scenarios |
| --- | --- |
| Air temperature increase/decrease | no |
| Specify minimum temperature | no |
| Specify maximum temperature | no |
| GHI profile increase/decrease | no |
| DNI profile increase/decrease | no |
| Wind speed increase/decrease | no |

Figure 22: Ambient air temperature (Annual profile)

Figure 23: Ambient air temperature (Heatmap)

Figure 24: Wind speed (Annual profile)

Figure 25: Wind speed (Heatmap)

Figure 26: Global horizontal irradiance (annual profile)

Figure 27: Global horizontal irradiance (Heatmap)

Figure 28: Direct normal irradiance (Annual profile)

Figure 29: Direct normal irradiance (Heatmap)

Figure 30: Horizontal infrared radiation (Annual profile)

Figure 31: Horizontal infrared radiation (Heatmap)

## 4.6 Additional information and data sources

This report includes map data © OpenStreetMap contributors, licensed under the Open Database License (ODbL).